Modbus RTU Communication Protocol for Energy Storage Inverters

Ver3.4 Contents

- Overview	3

- Physical Interface	3

  - Electrical Interface and Its Description	3

- Communication Protocol Description	3

  - Data Types	3

  - Communication Interval Requirements	3

  - Data Frame Format	3

  - Other Precautions	4

- Error Information and Data Handling	4

  - Error Code Definitions	4

- Detailed Protocol Description	5

  - Definition of Runtime Information Addresses	5

  - Definition of Set Parameter Addresses	40

- Protocol Usage Example	101

  - Reading Operational Information	101

  - Setting Operational Parameters	101

- Appendix	102

  - Appendix 1（M35000）	102

  - Appendix 2（M33092）	103

  - Appendix 3（M33095）	109

  - Appendix 4：Status Bit Definitions	114

  - Appendix 5：Low-Voltage Battery Number	116

  - Appendix 6：High-Voltage Battery Number	117

  - Appendix 7：Energy Storage Control Switch Status Description	119

Modified Version

| Version | Modified Content | Responsible person | Date |
| --- | --- | --- | --- |
| V000B000D000 | 1.New. | JW | 2026/02/04 |

- Overview

This protocol applies to the communication between our company's energy storage inverters and the host computer monitoring software. It adopts the MODBUS RTU communication protocol. This protocol enables real-time reading of the energy storage inverter's operational information and control operations on the energy storage inverter.

- Physical Interface

  - Electrical Interface and Its Description

Using RS485. The default parameters are as follows:

Slave Address: 1

Baud Rate: 9600 Parity: None Data Bits: 8

Stop Bits: 1

- Communication Protocol Description

  - Data Types

U16: 2-byte unsigned integer, high-order byte first, low-order byte last. S16: 2-byte signed integer, high-order byte first, low-order byte last.

U32: 4-byte unsigned integer, high-order byte first, low-order byte last, high-order word first, low-order word last.

S32: 4-byte signed integer, high-order byte first, low-order byte last, high-order word first, low-order word last.

  - Communication Interval Requirements

The query command frame interval must be greater than 300ms, and the control command interval must be greater than 700ms.

  - Data Frame Format

| Slave Address | Function Code | Data Field | CRC Code |
| --- | --- | --- | --- |
| 8-Bits | 8-Bits | Nx8-Bits | 16-Bits |

Slave Address: It must match the slave address of the inverter.

Function Code: It supports function codes 03H, 04H, 06H, and 10H.

| Function Code (Hexadecimal) | Name | Register Ad- dress | Function |
| --- | --- | --- | --- |
| 03H | Read Holding Regis- ters | 43000-44999 | Read Setting Register Con- tents |

| 04H | Read Input Registers | 33000-36999 25000~25999 | Read Inverter Information Content |
| --- | --- | --- | --- |
| 06H | Write Single Holding Register | 43000-44999 | Set Single Register Func- tion |
| 10H | Write Multiple Hold- ing Registers | 43000-44999 | Set Multiple Registers Function |

Data Field: The data field includes the start register address, data length, number of data bytes, and the data content itself. All values follow a high-byte-first, low-byte-last byte order.

CRC (Cyclic Redundancy Check) Code: The CRC verification method uses a table lookup ap- proach, with the low-order byte preceding the high-order byte in the check result.

  - Other Precautions

- Reading Unimplemented Registers: If a register address within the protocol range is not im- plemented by the chip, it returns 0x0000 and does not throw an exception.

- Writing to Unimplemented Registers: If a register address within the protocol range is not im- plemented by the chip, the data is discarded, but a normal response is still returned.

- Write Operation Restrictions: A single Modbus frame supports only one write operation. It is recommended to use function code 06 (Write Single Register).

- Broadcast Silence (Address 0xFF): When the slave station receives a frame with a "write" function code and the address 0xFF, it executes the action but does not return any response.

- General Address (Address 0xFE): The slave station can respond normally when it receives a frame with the address 0xFE, even if it differs from the inverter's actual address.

- Error Information and Data Handling

Slave Response (Hexadecimal):

| Slave Address | Function Code | Error Code | CRC Code |  |
| --- | --- | --- | --- | --- |
| xx | xx¦0x80 | xx | Low-order Byte | High-order Byte |
|  |  |  | xx | xx |

When the inverter's communication module detects an error other than a CRC code error, it must send a response back to the host. The highest bit of the function code is set to 1, which means 128 is added to the function code sent by the host.

  - Error Code Definitions

0x02 Illegal Data Address (related to the request)

0x03 Illegal Data Value (related to the request)

0x04 Service Fault (The inverter communication module encountered an internal failure while attempting to retrieve data during execution)

- Detailed Protocol Description

  - Definition of Operational Information Addresses

Corresponding to function code 0x04.

| Register Address (Decimal) | Description | Data Type | Unit | Remarks |
| --- | --- | --- | --- | --- |
| 35000 | Definition of Solis in- verter types | U16 |  | Refer to Appendix 1 for specific details (M35000) |
| 33000 | Product Model Number | U16 |  |  |
| 33001 | DSP Software Major Version | U16 |  | High-order Byte: Reserved, de- fault 0x00; any value other than 0x00 indicates the Sub-DSP Major Version. Low-order Byte: The Main DSP Major Version (displayed in hex- adecimal). Description: Together with the low-order byte of register 33021, this forms the complete Main DSP Software Version Number. Example: If the low-order byte of register 33001 is 0x1A and the low-order byte of register 33021 is 0x0B, then the Main DSP Soft- ware Version Number is 1A0B (hexadecimal). |
| 33002 | HMI Software Major Version | U16 |  | High-order byte: Reserved, default 0x00 Low-order byte: Major version number (displayed in hexadecimal) Description: Together with the low-order byte of register 33069, this forms the complete HMI soft- ware version number. Example: If the low-order byte of register 33002 is 0x1C and the low-order byte of register 33069 is 0x06, then the HMI software ver- sion number is 1C06. |
| 33004 | Inverter Serial Number SN_1 | U16 |  | Inverter Serial Number (Hexade- cimal Display) |

| 33005 | Inverter Serial Number SN_2 | U16 |  | Example: If the value uploaded from register 33004 is ‘01’, and the value from register 33005 is ‘23’, then the cor- responding display is ‘0123’. When the two-digit Model Number (high byte of register 33000 is 0x00), only the high-order 15 bytes are valid as the SN. When the four-digit Model Number is used, only the high-order 16 bytes are valid as the SN. The unused data bits of the Inverter Serial Number have a value of 0. Register 33004 is the highest-order byte, and register 33019 is the low- est-order byte. |
| --- | --- | --- | --- | --- |
| 33006 | Inverter Serial Number SN_3 | U16 |  |  |
| 33007 | Inverter Serial Number SN_4 | U16 |  |  |
| 33008 | Inverter Serial Number SN_5 | U16 |  |  |
| 33009 | Inverter Serial Number SN_6 | U16 |  |  |
| 33010 | Inverter Serial Number SN_7 | U16 |  |  |
| 33011 | Inverter Serial Number SN_8 | U16 |  |  |
| 33012 | Inverter Serial Number SN_9 | U16 |  |  |
| 33013 | Inverter Serial Number SN_10 | U16 |  |  |
| 33014 | Inverter Serial Number SN_11 | U16 |  |  |
| 33015 | Inverter Serial Number SN_12 | U16 |  |  |
| 33016 | Inverter Serial Number SN_13 | U16 |  |  |
| 33017 | Inverter Serial Number SN_14 | U16 |  |  |
| 33018 | Inverter Serial Number SN_15 | U16 |  |  |
| 33019 | Inverter Serial Number SN_16 | U16 |  |  |
| 33021 | DSP Software Sub Ver- sion | U16 |  | High-order byte: Reserved, default 0x00; Low-order byte: Main DSP Sub version number (displayed in hex- adecimal) Description: Together with the low-order byte of register 33001, this forms the complete Main DSP Software Version Number. Example: If the low-order byte of register 33001 is 0x1A and the low-order byte of register 33021 is 0x0B, then the Main DSP Software Version Number is 1A0B. |

| 33029~ 33030 | Total PV Energy Gen- eration | U32 | 1kWh | For Hybrid Energy Storage Inverter models: Indicates the PV energy generation data of this unit itself. For S6 Single-Phase Low-Voltage AC-Coupled models: Indicates the PV energy generation data of the paralleled PV inverter(s). |
| --- | --- | --- | --- | --- |
| 33035 | Today's PV Energy Generation | U16 | 0.1kW h |  |
| 33041 | Maximum Charge/Discharge Cur- rent of this device’s battery | U16 | 0.1A |  |
| 33042 | Rated Output Current of this device‘s AC Grid Port | U16 | 0.1A |  |
| 33043 | Battery 1 Temperature | S16 | 0.1℃ | Description: From Battery 1 BMS |
| 33046 | Inverter Battery MOS- FET Temperature | S16 | 0.1℃ | Description: Supported by S6 Gen- eration Energy Storage Models |
| 33048 | DC Input Type | U16 |  | 0: Indicates 1 input 1: Indicates 2 inputs 2: Indicates 3 inputs 3: Indicates 4 inputs …… |
| 33049 | PV DC Voltage 1 | U16 | 0.1V |  |
| 33050 | PV DC Current 1 | U16 | 0.1A |  |
| 33051 | PV DC Voltage 2 | U16 | 0.1V |  |
| 33052 | PV DC Current 2 | U16 | 0.1A |  |
| 33053 | PV DC Voltage 3 | U16 | 0.1V |  |
| 33054 | PV DC Current 3 | U16 | 0.1A |  |
| 33055 | PV DC Voltage 4 | U16 | 0.1V |  |
| 33056 | PV DC Current 4 | U16 | 0.1A |  |
| 33057~ 33058 | Total PV Input Power | U32 | 1W | Represents the real-time total PV power of this unit |
| 33059 | PV DC Voltage 5 | U16 | 0.1V |  |
| 33060 | PV DC Current 5 | U16 | 0.1A |  |
| 33061 | PV DC Voltage 6 | U16 | 0.1V |  |
| 33062 | PV DC Current 6 | U16 | 0.1A |  |
| 33063 | PV DC Voltage 7 | U16 | 0.1V |  |
| 33064 | PV DC Current 7 | U16 | 0.1A |  |
| 33065 | PV DC Voltage 8 | U16 | 0.1V |  |
| 33066 | PV DC Current 8 | U16 | 0.1A |  |
| 33067 | This device’s Rated Apparent Power | U16 | 10VA |  |
| 33068 | Safety Regulation Ver- | U16 |  | Refer to the "Safety Ver" column in |

|  | sion Number |  |  | the "National Grid Protection Stan- dard Settings Table" |
| --- | --- | --- | --- | --- |
| 33069 | HMI Software Sub Ver- sion | U16 |  | High-order byte: Reserved, default 0x00 Low-order byte: Sub version num- ber (displayed in hexadecimal) Description: Together with the low-order byte of register 33002, this forms the HMI software version number. Example: If the low-order byte of register 33002 is 0x1C and the low-order byte of register 33069 is 0x06, then the HMI software ver- sion number is V1CB06 (or 1C06, the prefix V and infix B may be specific display format). |
| 33070 | Warning/Fault Message Data | U16 |  | Refer to Appendix 3 (M33095) for details. Description: Used in conjunction with register address 33095 to sub- divide and display detailed fault information. 。 |
| 33073 | AB Line Voltage / A Phase Voltage | U16 | 0.1V | For 5G/S5 generation energy sto- rage units: represents the internal inverter-side AC voltage. For S6 generation energy storage units: represents the AC voltage at the inverter's AC Grid port. Single-phase energy storage units use A phase voltage. S6 Single-Phase High-Voltage US Version Energy Storage Inverter: L1-N voltage. |
| 33074 | BC Line Voltage / B Phase Voltage | U16 | 0.1V | S6 Single-Phase High-Voltage US Version Energy Storage Inverter: L2-N voltage. |
| 33075 | CA Line Voltage / C Phase Voltage | U16 | 0.1V | S6 Single-Phase High-Voltage US Version Energy Storage Inverter: L1-L2 voltage. |
| 33076 | A Phase Current | U16 | 0.1A | For 5G/S5 generation energy sto- rage units: represents the internal inverter-side AC current. For S6 generation energy storage |

|  |  |  |  | units: represents the AC current at the inverter's AC Grid port. Single-phase energy storage units use A phase current. S6 Single-Phase High-Voltage US Version Energy Storage Inverter: L1-N current. |
| --- | --- | --- | --- | --- |
| 33077 | B Phase Current | U16 | 0.1A | S6 Single-Phase High-Voltage US Version Energy Storage Inverter: L2-N current. |
| 33078 | C Phase Currnt | U16 | 0.1A | S6 Single-Phase High-Voltage US Version Energy Storage Inverter: This register is invalid when N (Neutral) is connected; when N is not connected, this register represents the L1-L2 current. |
| 33079~ 33080 | Active Power Value | S32 | 1W | Active power of the inver- ter/rectifier. |
| 33081~ 33082 | Reactive Power Value | S32 | 1Var | Reactive power of the inver- ter/rectifier. |
| 33083~ 33084 | Apparent Power Value | S32 | 1VA | Apparent power of the inver- ter/rectifier. |
| 33092 | National Standard Number | U16 |  | Refer to Appendix 2 (M33092) for details. |
| 33093 | Inverter Module Tem- perature Note: AC NTC (IGBT) | S16 | 0.1℃ |  |
| 33094 | Grid Frequency | U16 | 0.01Hz |  |
| 33095 | Inverter Current Status | U16 |  | Refer to Appendix 3 (M33095) for details. Description: Used in conjunction with register address 33070 to sub- divide and display detailed informa- tion. |
| 33096 | Lead-Acid Battery Am- bient Temperature | S16 | 0.1℃ |  |
| 33098 | Current DRM Status | U16 |  |  |
| 33121 | Operating Status | U16 |  | Refer to Appendix 4: Status Bit De- finitions for details. |
| 33123 | Standard Operating Mode Startup Status | U16 |  | Each bit indicates the startup status of an operating mode: 0 = not started, 1 = started. BIT00: Volt-watt (Voltage vs. Ac- tive Power). |

|  |  |  |  | BIT01: Volt-var (Voltage vs. Reac- tive Power). BIT02: Fixed power factor. BIT03: Fixed reactive power. BIT04: Power-PF (Active Power vs. Power Factor). BIT05: Power-Q (Active Power vs. Reactive Power). |
| --- | --- | --- | --- | --- |
| 33133 | Battery 1 Real-time Voltage | U16 | 0.1V | Description: Battery 1 real-time voltage value. |
| 33134 | Battery 1 Real-time Current | S16 | 0.1A | Description: - Charge/discharge direction is determined by register 33135; - The absolute value of this regis- ter represents the real-time current of Battery 1. |
| 33135 | Battery 1 Real-time Charge/Discharge Di- rection | U16 |  | 0: Charging; 1: Discharging. |
| 33137 | Backup Port AC Vol- tage A | U16 | 0.1V | Description: - Backup port information for single-phase systems; - For split-phase systems, represents L1-N voltage when con- nected to Neutral; - For three-phase systems, represents L1-N voltage. |
| 33138 | Backup Port AC Cur- rent A | U16 | 0.1A | Description: - Backup port information for single-phase systems; - For split-phase systems, represents current on L1 line; - For three-phase systems, represents current on L1 line. |
| 33139 | Battery 1 State of Charge (SOC) | U16 | 1% | 100<-->100% |
| 33140 | Battery 1 State of Health (SOH) | U16 | 1% | 100<-->100% |
| 33147 | Grid-side Home Load Power (Low Register) | U16 | 1W | Represents only grid-side home loads, excluding Backup loads; for three-phase systems, represents the total active power sum of all grid-side phase loads. Description: |

|  |  |  |  | - When the actual grid-side load exceeds 65 kW, it combines with register 34343 to form a U32 data type representing the grid-side load power. Combination example: Power = 700,000 W; 700,000 (Dec) = 0x00011170 (Hex); therefore, register 34343 data is 0x0001, and register 33147 data is 0x1170. |
| --- | --- | --- | --- | --- |
| 33148 | Backup Load Power (Low Register) | S16 | 1W | A positive value indicates power flowing out of the energy storage inverter Backup port, and a negative value indicates power flowing into the energy storage inverter Backup port. Description: - For models with a capacity not exceeding 20 kW, use only register 33148. - For models exceeding 20 kW, combine with register 34344 to form an S32 data type representing the Backup load power. See the combination examples below for details. - In parallel systems, the master controller reads the Backup port active power values from each in- verter and sums them. Combination examples: - Power = 700,000 W; 700,000 (Dec) = 0x00011170 (Hex); thus, register 34344 data is 0x0001, and register 33148 data is 0x1170. - Power = -1,000 W; -1,000 (Dec) = 0xFFFCFC18 (Hex); thus, register 34344 data is 0xFFF, and register 33148 data is 0xFC18. |
| 33149~ 33150 | Battery 1 Real-time Power | S32 | 1W | Description: (1) The charge/discharge direction is determined by register 33135. |

|  |  |  |  | - The absolute value of this regis- ter represents the real-time power of Battery 1. - For models with a single battery port, this represents the power at the energy storage inverter's battery current port. For models with two independent battery ports, this represents the power at the energy storage inverter's battery current port 1. |
| --- | --- | --- | --- | --- |
| 33151~ 33152 | Inverter AC Grid Port Real-time Total Active Power | S32 | 1W | Positive value: Power flowing out of the AC Grid port; Negative value: Power flowing into the AC Grid port |
| 33153 | Backup Port AC Vol- tage B | U16 | 0.1V | 10<-->1V，Description: - For single-phase systems, data is 0. - For split-phase systems, when connected to Neutral, represents L2-N voltage. - For three-phase systems, represents L2-N voltage. |
| 33154 | Backup Port AC Cur- rent B | U16 | 0.1A | 10<-->1V，Description: - For single-phase systems, data is 0. - For split-phase systems, represents current on the L2 line. - For three-phase systems, represents current on the L2 line. |
| 33155 | Backup Port AC Vol- tage C | U16 | 0.1V | 10<-->1V，Description: - For single-phase systems, data is 0. - For split-phase systems, data is 0. - For three-phase systems, represents L3-N voltage. |
| 33156 | Backup Port AC Cur- rent C | U16 | 0.1A | 10<-->1A，Description: - For single-phase systems, data is 0. - For split-phase systems, data is 0. - For three-phase systems, represents current on the L3 line. |

| 33161~ 33162 | Battery Total Charging Energy | U32 | 1kWh | Description: For models with dual battery ports, this value represents the cumulative charging energy of both batteries. |
| --- | --- | --- | --- | --- |
| 33163 | Battery Daily Charging Energy | U16 | 0.1kW h | Description: For models with dual battery ports, this value represents the cumulative charging energy of both batteries. |
| 33165~ 33166 | Battery Total Discharg- ing Energy | U32 | 1kWh | Description: For models with dual battery ports, this value represents the cumulative charging energy of both batteries. |
| 33167 | Battery Daily Dis- charging Energy | U16 | 0.1kW h | Description: For models with dual battery ports, this value represents the cumulative charging energy of both batteries. |
| 33169~ 33170 | Grid Total Power Con- sumption | U32 | 1kWh | Description: Represents the cumu- lative energy consumed from the public grid |
| 33171 | Grid Daily Power Con- sumption | U16 | 0.1kW h | Description: Represents the cumu- lative energy consumed from the public grid |
| 33173~ 33174 | Grid Total Power Feed-in | U32 | 1kWh | Description: Represents the cumu- lative energy feed in to the public grid |
| 33175 | Grid Daily Power Feed-in | U16 | 0.1kW h | Description: Represents the cumu- lative energy feed in to the public grid |
| 33177~ 33178 | Load Total Power Con- sumption | U32 | 1kWh | Description: Represents the cumu- lative energy consumption of the Grid-side Home Load AND the Backup Load. |
| 33179 | Load Daily Power Consumption | U16 | 0.1kW h | Description: Represents the cumu- lative energy consumption of the Grid-side Home Load AND the Backup Load. |
| 33186~ 33187 | Inverter AC Grid Port Total Power Feed-in | U32 | 1kWh |  |
| 33188~ 33189 | Inverter AC Grid Port Total Power Consump- tion | U32 | 1kWh |  |
| 33221 | Italian Single Test Function Setting (Ital- ian Self-check Project - | U16 |  | 0---Null 01---59.S1(253.0V 3000ms) 02---59.S2(264.5V 200ms) |

|  | Single Item Self-check) |  |  | 03---27.S1(195.5V 1500ms) 04---27.S2( 34.5V 200ms) 05---81>.S1(50.2Hz 100ms) 06---81<.S1(49.8 Hz 100ms) 07---81>.S2F(51.5Hz 100ms) 08---81<.S2F(47.5 Hz 100ms) 09---81>.S2S(51.5Hz 1000ms) 10---81<.S2S(47.5 Hz 4000ms) 11---59.S1 PhaseB(253.0V 3000ms) 12---59.S2 PhaseB (264.5V 200ms) 13---27.S1 PhaseB (195.5V 1500ms) 14---27.S2 PhaseB ( 34.5V 200ms) 15---81>.S1 PhaseB (50.2Hz 100ms) 16---81<.S1 PhaseB (49.8 Hz 100ms) 17---81>.S2F PhaseB (51.5Hz 100ms) 18---81<.S2F PhaseB (47.5 Hz 100ms) 19---81>.S2S PhaseB (51.5Hz 1000ms) 20---81<.S2S PhaseB (47.5 Hz 4000ms) 21---59.S1 PhaseC (253.0V 3000ms) 22---59.S2 PhaseC (264.5V 200ms) 23---27.S1 PhaseC (195.5V 1500ms) 24---27.S2 PhaseC ( 34.5V 200ms) 25---81>.S1 PhaseC (50.2Hz 100ms) 26---81<.S1 PhaseC (49.8 Hz 100ms) 27---81>.S2F PhaseC (51.5Hz 100ms) 28---81<.S2F PhaseC (47.5 Hz |
| --- | --- | --- | --- | --- |

|  |  |  |  | 100ms) 29---81>.S2S PhaseC (51.5Hz 1000ms) 30---81<.S2S PhaseC (47.5 Hz 4000ms) The self-check items for Phase B and Phase C are only supported by three-phase energy storage ma- chines. |
| --- | --- | --- | --- | --- |
| 33222 | Italian One-Key Full Test (Complete Self-check of Italian Self-check Items 01-10) | U16 |  | Value: Start Complete Self Test 1—In single-item self-check state. 2—In one-key full-test state. |
| 33223 | 59.S1 Measurement Voltage Value | U16 | 0.1V | 10<-->1V |
| 33224 | 59.S1 Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33225 | 59.S2 Measurement Voltage Value | U16 | 0.1V | 10<-->1V |
| 33226 | 59.S2 Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33227 | 27.S1 Measurement Voltage Value | U16 | 0.1V | 10<-->1V |
| 33228 | 27.S1 Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33229 | 27.S2 Measurement Voltage Value | U16 | 0.1V | 10<-->1V |
| 33230 | 27.S2 Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33231 | 81>.S1 Measurement Frequency Value | U16 | 0.01Hz | 100<-->1Hz |
| 33232 | 81>.S1 Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33233 | 81<.S1 Measurement Frequency Value | U16 | 0.01Hz | 100<-->1Hz |
| 33234 | 81<.S1 Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33235 | 81>.S2F Measurement Frequency Value | U16 | 0.01Hz | 100<-->1Hz |
| 33236 | 81>.S2F Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33237 | 81<.S2F Measurement Frequency Value | U16 | 0.01Hz | 100<-->1Hz |
| 33238 | 81<.S2F Measurement | U16 | 1ms | 1<-->1ms |

|  | Time Value |  |  |  |
| --- | --- | --- | --- | --- |
| 33239 | 81>.S2S Measurement Frequency Value | U16 | 0.01Hz | 100<-->1Hz |
| 33240 | 81>.S2S Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33241 | 81<.S2S Measurement Frequency Value | U16 | 0.01Hz | 100<-->1Hz |
| 33242 | 81<.S2S Measurement Time Value | U16 | 1ms | 1<-->1ms |
| 33245 | Parallel Inverter Power | U16 | 0.1kW | Applicable only to single-phase low-voltage AC Coupled systems. |
| 33246 | Parallel Inverter CT Detection Switch | U16 |  | Value: 0: Off. When register 33245 value is greater than 500W, it indi- cates that the parallel inverter has a CT installed and power is present. Value: 1： On. Regardless of the value in register 33245, the host computer must display the power value. Note: Applicable only to sin- gle-phase low-voltage AC Coupled systems. |
| 33251 | Meter AC Voltage A | U16 | 0.1V | 10<-->1V - Registers 33251~33286 represent data read from the exter- nal meter/CT itself, when installed on the public grid side or the load side. - When the meter/CT is installed on the public grid side, reading these register addresses indicates AC information from the public grid side. - When the meter is installed on the load side, refer to the description in registers 33540-33575. |
| 33252 | Meter AC Current A | U16 | 0.01A | 100<-->1A |
| 33253 | Meter AC Voltage B | U16 | 0.1V | 10<-->1V |
| 33254 | Meter AC Current B | U16 | 0.01A | 100<-->1A |
| 33255 | Meter AC Voltage C | U16 | 0.1V | 10<-->1V |
| 33256 | Meter AC Current C | U16 | 0.01A | 100<-->1A |
| 33257~ 33258 | Meter Active Power A | S32 | 1W | 1000<-->1kW, Description: When the external meter/CT is in- stalled on the public grid side, a |

|  |  |  |  | positive value indicates power flowing toward the public grid, while a negative value indicates power being drawn from the public grid. |
| --- | --- | --- | --- | --- |
| 33259~ 33260 | Meter Active Power B | S32 | 1W | 1000<-->1kW, Description: When the external meter/CT is in- stalled on the public grid side, a positive value indicates power flowing toward the public grid, while a negative value indicates power being drawn from the public grid. |
| 33261~ 33262 | Meter Active Power C | S32 | 1W | 1000<-->1kW, Description: When the external meter/CT is in- stalled on the public grid side, a positive value indicates power flowing toward the public grid, while a negative value indicates power being drawn from the public grid. |
| 33263~ 33264 | Meter Total Active Power | S32 | 1W | 1000<-->1kW, Description: When the external meter/CT is in- stalled on the public grid side, a positive value indicates power flowing toward the public grid, while a negative value indicates power being drawn from the public grid. |
| 33265~ 33266 | Meter Reactive Power A | S32 | 1Var | 1<-->1Var |
| 33267~ 33268 | Meter Reactive Power B | S32 | 1Var | 1<-->1Var |
| 33269~ 33270 | Meter Reactive Power C | S32 | 1Var | 1<-->1Var |
| 33271~ 33272 | Meter Total Reactive Power | S32 | 1Var | 1<-->1Var |
| 33273~ 33274 | Meter Apparent Power A | S32 | 1VA | 1<-->1VA |
| 33275~ 33276 | Meter Apparent Power B | S32 | 1VA | 1<-->1VA |
| 33277~ 33278 | Meter Apparent Power C | S32 | 1VA | 1<-->1VA |
| 33279~ | Meter Total Apparent | S32 | 1VA | 1<-->1VA |

| 33280 | Power |  |  |  |
| --- | --- | --- | --- | --- |
| 33281 | Meter Power Factor | S16 | 0.01 | 100<-->1.0 Range: -1.0~-0.8 , +0.8~+1.0 |
| 33282 | Meter Grid Frequency | U16 | 0.01Hz | 100<-->1Hz |
| 33283~ 33284 | Meter Total Active Energy Imported from Grid | U32 | 0.01 kWh | 100<-->1kWh |
| 33285~ 33286 | Meter Total Active Energy Exported to Grid | U32 | 0.01 kWh | 100<-->1kWh |
| 33289 | Optimal Revenue Func- tion Version Identifica- tion | U16 |  | Optimization Revenue V2 Function Enable Status: 0xAA55: Active; Others: Inactive |
| 33295 | Battery 1 BMS Real-time Status | U16 |  | bit00~01: Forced Charging Request, 0—Invalid, 1—No Request, 2—Request, 3—Invalid bit02~03: Auxiliary Heating Request, 0—Invalid, 1—No Request, 2—Request, 3—Invalid bit04~15: Reserved |
| 33388 | Parallel System Inverter Online Status | U16 |  | Each BIT indicates the online status of the corresponding inverter ID. BIT00: Not used. BIT01~15: Indicate the online status of inverters with IDs 1~15; 0 = Of- fline, 1 = Online. Note: When the App reads BIT01 and BIT02 of register 33097 both as 1 (indicating it is the master inverter of the parallel system), it will then operate (including reading/writing) the registers of each inverter based on the online status in register 33338 and the corresponding inver- ter ID. |
| 33339 | Inverter Warning | U16 |  | For details, refer to Appendix 4: Status Bit Definitions. |
| 33470 | 59.S1 Measurement Voltage Value (Phase B) | U16 | 0.1V | 10<-->1V. Note: Registers 33470-33509 are used for the Phase B and Phase C results of the Italian CEI 0-21 stan- |

|  |  |  |  | dard self-test function and are ap- plicable only to three-phase energy storage machines. |
| --- | --- | --- | --- | --- |
| 33471 | 59.S1 Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33472 | 59.S2 Measurement Voltage Value (Phase B) | U16 | 0.1V | 10<-->1V |
| 33473 | 59.S2 Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33474 | 27.S1 Measurement Voltage Value (Phase B) | U16 | 0.1V | 10<-->1V |
| 33475 | 27.S1 Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33476 | 27.S2 Measurement Voltage Value (Phase B) | U16 | 0.1V | 10<-->1V |
| 33477 | 27.S2 Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33478 | 81>.S1 Measurement Frequency Value (Phase B) | U16 | 0.01Hz | 100<-->1Hz |
| 33479 | 81>.S1 Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33480 | 81<.S1 Measurement Frequency Value (Phase B) | U16 | 0.01Hz | 100<-->1Hz |
| 33481 | 81<.S1 Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33482 | 81>.S2F Measurement Frequency Value (Phase B) | U16 | 0.01Hz | 100<-->1Hz |
| 33483 | 81>.S2F Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33484 | 81<.S2F Measurement Frequency Value (Phase B) | U16 | 0.01Hz | 100<-->1Hz |
| 33485 | 81<.S2F Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33486 | 81>.S2S Measurement Frequency Value (Phase B) | U16 | 0.01Hz | 100<-->1Hz |
| 33487 | 81>.S2S Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33488 | 81<.S2S Measurement Frequency Value (Phase | U16 | 0.01Hz | 100<-->1Hz |

|  | B) |  |  |  |
| --- | --- | --- | --- | --- |
| 33489 | 81<.S2S Measurement Time Value (Phase B) | U16 | 1ms | 1<-->1ms |
| 33490 | 59.S1 Measurement Voltage Value (Phase C) | U16 | 0.1V | 10<-->1V |
| 33491 | 59.S1 Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33492 | 59.S2 Measurement Voltage Value (Phase C) | U16 | 0.1V | 10<-->1V |
| 33493 | 59.S2 Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33494 | 27.S1 Measurement Voltage Value (Phase C) | U16 | 0.1V | 10<-->1V |
| 33495 | 27.S1 Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33496 | 27.S2 Measurement Voltage Value (Phase C) | U16 | 0.1V | 10<-->1V |
| 33497 | 27.S2 Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33498 | 81>.S1 Measurement Frequency Value (Phase C) | U16 | 0.01Hz | 100<-->1Hz |
| 33499 | 81>.S1 Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33500 | 81<.S1 Measurement Frequency Value (Phase C) | U16 | 0.01Hz | 100<-->1Hz |
| 33501 | 81<.S1 Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33502 | 81>.S2F Measurement Frequency Value (Phase C) | U16 | 0.01Hz | 100<-->1Hz |
| 33503 | 81>.S2F Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33504 | 81<.S2F Measurement Frequency Value (Phase C) | U16 | 0.01Hz | 100<-->1Hz |
| 33505 | 81<.S2F Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33506 | 81>.S2S Measurement Frequency Value (Phase C) | U16 | 0.01Hz | 100<-->1Hz |
| 33507 | 81>.S2S Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |

| 33508 | 81<.S2S Measurement Frequency Value (Phase C) | U16 | 0.01Hz | 100<-->1Hz |
| --- | --- | --- | --- | --- |
| 33509 | 81<.S2S Measurement Time Value (Phase C) | U16 | 1ms | 1<-->1ms |
| 33512 | Inverter AC Grid Port Phase A Active Power | S16 | 10W | Positive value indicates power flowing out of the energy storage inverter, negative value indicates power flowing into the energy sto- rage inverter. Range: -327,680 W to 327,680 W. Description: - For single-phase energy storage systems, Phase A data is used by default. - For split-phase energy storage systems, Phase A and Phase B data are used by default. |
| 33513 | Inverter AC Grid Port Phase A Reactive Power | S16 | 10Var | Range: -327680Var~327680Var |
| 33514 | Inverter AC Grid Port Phase A Apparent Pow- er | S16 | 10VA | Range: 0VA~327680VA |
| 33515 | Inverter AC Grid Port Phase B Active Power | S16 | 10W | Positive value indicates power flowing out of the energy storage inverter, negative value indicates power flowing into the energy sto- rage in-verter. Range: -327680W~327680W； |
| 33516 | Inverter AC Grid Port Phase B Reactive Pow- er | S16 | 10Var | Range: -327680Var~327680Var |
| 33517 | Inverter AC Grid Port Phase B Apparent Pow- er | S16 | 10VA | Range: 0VA~327680VA |
| 33518 | Inverter AC Grid Port Phase C Active Power | S16 | 10W | Positive value indicates power flowing out of the energy storage inverter, negative value indicates power flowing into the energy sto- rage inverter. Range: -327680W~327680W； |
| 33519 | Inverter AC Grid Port Phase C Reactive Pow- er | S16 | 10Var | Range: -327680Var~327680Var |

| 33520 | Inverter AC Grid Port Phase C Apparent Pow- er | S16 | 10VA | Range: 0VA~327680VA |
| --- | --- | --- | --- | --- |
| 33521 | Inverter Backup Port Phase A Active Power | S16 | 10W | A positive value indicates power flowing out of the Backup port, while a negative value indicates power flowing into the Backup port. Range: -327680W~327680W； For U.S. models, it represents the active power calculated using L1-N voltage and L1 current. |
| 33522 | Inverter Backup Port Phase A Reactive Power | S16 | 10Var | Range: -327680Var~327680Var For U.S. models, it represents the reactive power calculated using L1-N voltage and L1 current. |
| 33523 | Inverter Backup Port Phase A Apparent Pow- er | S16 | 10VA | Range: 0VA~327680VA； For U.S. models, it represents the apparent power calculated using L1-N voltage and L1 current. |
| 33524 | Inverter Backup Port Phase B Active Power | S16 | 10W | A positive value indicates power flowing out of the Backup port, while a negative value indicates power flowing into the Backup port. Range: -327680W~327680W； For U.S. models, it represents the active power calculated using L2-N voltage and L2 current. |
| 33525 | Inverter Backup Port Phase B Reactive Pow- er | S16 | 10Var | Range: -327680Var~327680Var For U.S. models, it represents the reactive power calculated using L2-N voltage and L2 current. |
| 33526 | Inverter Backup Port Phase B Apparent Pow- er | S16 | 10VA | Range: 0VA~327680VA； For U.S. models, it represents the apparent power calculated using L2-N voltage and L2 current. |
| 33527 | Inverter Backup Port Phase C Active Power | S16 | 10W | A positive value indicates power flowing out of the Backup port, while a negative value indicates power flowing into the Backup port. Range: -327680W~327680W； For U.S. models, the value is 0. |
| 33528 | Inverter Backup Port Phase C Reactive Pow- er | S16 | 10Var | Range: -327680Var~327680Var For U.S. models, the value is 0. |

| 33529 | Inverter Backup Side Phase C Apparent Pow- er | S16 | 10VA | Range: 0VA~327680VA； For U.S. models, the value is 0. |
| --- | --- | --- | --- | --- |
| 33530 | Generator Phase A Ac- tive Power | S16 | 10W | Single-phase systems use Phase A power. |
| 33531 | Generator Daily Power Generation | U16 | 0.1kW h | 10<-->1kWh |
| 33532~ 33533 | Generator Total Power Generation | U32 | 1kWh | 1<-->1kWh |
| 33534 | Generator Phase B Ac- tive Power | S16 | 10W | 100<-->1kW |
| 33535 | Generator Phase C Ac- tive Power | S16 | 10W | 100<-->1kW |
| 33577 | Inverter AC Grid Port Daily Power Export | U16 | 0.1kW h | 10 <--> 1kWh |
| 33578 | Inverter AC Grid Port Daily Power Import | U16 | 0.1kW h | 10 <--> 1kWh |
| 33580~ 33581 | Grid-side Home Load Total Power Consump- tion | U32 | 1kWh |  |
| 33586 | Grid-side Home Load Daily Power Consump- tion | U16 | 0.1kW h |  |
| 33590~ 33591 | Backup Load Total Power Consumption | U32 | 1kWh | Standalone Mode: Represents the energy flowing out of the local unit's Backup port. Parallel Mode: The master unit's Backup load energy data represents the total Backup energy of the entire parallel system, while slave units represent the energy flowing out of their respective Backup ports. |
| 33596 | Backup Load Daily Power Consumption | U16 | 0.1kW h | 10 <--> 1kWh |
| 34200 | LG Battery 10H/16H Master Battery SOC | U16 | 0.001 | 1000<-->100% From LG High Voltage Battery BMS |
| 34201 | LG Battery 10H/16H Master Battery SOH | U16 | 0.001 | 1000<-->100% |
| 34202 | LG Battery 10H/16H Master Battery Voltage | U16 | 0.1V | 10<-->1V |
| 34203 | LG Battery 10H/16H Master Battery Current | S16 | 0.1V | 10<-->1A Positive indicates charging, negative indicates discharging. |

| 34204 | LG Battery 10H/16H Master Battery Maxi- mum Charging Power | U16 | 1W | 1<-->1W |
| --- | --- | --- | --- | --- |
| 34205 | LG Battery 10H/16H Master Battery Maxi- mum Discharging Pow- er | U16 | 1W | 1<-->1W |
| 34206 | LG Battery 10H/16H Master Battery DCDC Firmware Version (Main) | U16 |  |  |
| 34207 | LG Battery 10H/16H Master Battery DCDC Firmware Version (Test) | U16 |  |  |
| 34208 | LG Battery 10H/16H Master Battery BMS Firmware Version High Byte | U16 |  |  |
| 34209 | LG Battery 10H/16H Master Battery BMS Firmware Version Low Byte | U16 |  |  |
| 34210 | LG Battery 10H/16H Master Battery Fault ID | U16 |  |  |
| 34211 | LG Battery 10H/16H Master Battery Diag- nostic Result | U16 |  | 0: No abnormality detected 1: Level 1 Warning – Warning1 (limits available battery charg- ing/discharging power) 2: Level 2 Warning – Warning2 (battery actively switches to Stand- by state) 3: Fault (battery actively switches to Fault state) |
| 34212 | LG Battery 10H/16H Master Battery Sta- tus/Mode | U16 |  | 0: Initial State 1: Standby State 3: Operation State 4: Update State (battery firmware update via inverter) 5: Fault State (cannot recover auto- matically) 6: Battery Self Update 10: Power-saving State |
| 34213 | LG Battery 10H/16H Master Battery Current | S16 | 1W | 1<-->1W Positive value indicates charging. |

|  | Power |  |  |  |
| --- | --- | --- | --- | --- |
| 34214 | LG Battery 10H/16H Master Battery Maxi- mum Temperature | S16 | 0.1Deg c | 10<-->1DegC |
| 34215 | LG Battery 10H/16H Master Battery Status Flags | U16 |  | BIT00: Full Charge Flag – 0: Not fully charged, 1: Fully charged BIT01: Full Discharge Flag – 0: Not fully discharged, 1: Fully discharged BIT02: CB Status – 0: Open, 1: Closed BIT03: Power-saving Mode Entry Flag – 0: Available, 1: Unavailable BIT04–15: Reserved |
| 34216 | LG Battery 10H/16H Secondary Battery SOC | U16 | 0.001 | 1000<-->100% From LG High Voltage Battery BMS |
| 34217 | LG Battery 10H/16H Secondary Battery SOH | U16 | 0.001 | 1000<-->100% |
| 34218 | LG Battery 10H/16H Secondary Battery Vol- tage | U16 | 0.1V | 10<-->1V |
| 34219 | LG Battery 10H/16H Secondary Battery Current | S16 | 0.1A | 10<-->1A Positive indicates charging, negative indicates discharging. |
| 34220 | LG Battery 10H/16H Secondary Battery Maximum Charging Power | U16 | 1W | 1<-->1W |
| 34221 | LG Battery 10H/16H Secondary Battery Maximum Discharging Power | U16 | 1W | 1<-->1W |
| 34222 | LG Battery 10H/16H Secondary Battery DCDC Firmware Ver- sion (Main) | U16 |  |  |
| 34223 | LG Battery 10H/16H Secondary Battery DCDC Firmware Ver- sion (Test) | U16 |  |  |
| 34224 | LG Battery 10H/16H Secondary Battery BMS Firmware Version High Byte | U16 |  |  |

| 34225 | LG Battery 10H/16H Secondary Battery BMS Firmware Version Low Byte | U16 |  |  |
| --- | --- | --- | --- | --- |
| 34226 | LG Battery 10H/16H Secondary Battery Fault ID | U16 |  |  |
| 34227 | LG Battery 10H/16H Secondary Battery Di- agnostic Result | U16 |  | 0: No abnormality detected 1: Level 1 Warning – Warning1 (limits available battery charg- ing/discharging power) 2: Level 2 Warning – Warning2 (battery actively switches to Stand- by state) 3: Fault (battery actively switches to Fault state) |
| 34228 | LG Battery 10H/16H Secondary Battery Sta- tus/Mode | U16 |  | 0: Initial State 1: Standby State 3: Operation State 4: Update State (battery firmware update via inverter) 5: Fault State (cannot recover auto- matically) 6: Battery Self Update 10: Power-saving State |
| 34229 | LG Battery 10H/16H Secondary Battery Current Power | S16 | 1W | 1<-->1W Positive value indicates charging. |
| 34230 | LG Battery 10H/16H Secondary Battery Maximum Temperature | S16 | 0.1Deg C | 10<-->1DegC |
| 34231 | LG Battery 10H/16H Secondary Battery Sta- tus Flags | U16 |  | BIT00: Full Charge Flag – 0: Not fully charged, 1: Fully charged BIT01: Full Discharge Flag – 0: Not fully discharged, 1: Fully discharged BIT02: CB Status – 0: Open, 1: Closed BIT03: Power-saving Mode Entry Flag – 0: Available, 1: Unavailable BIT04–15: Reserved |
| 34240 | AFCI Board Software Version | U16 |  | (Displayed in Hexadecimal) Description: This indicates the ver- sion number of the AFCI detection board. |

|  |  |  |  | The high byte represents the major version number of the AFCI detec- tion board, and the low byte represents the minor version num- ber of the AFCI detection board. For example, 0xAABB: AA represents the major version number of the AFCI detection board, and BB represents the minor version number of the AFCI detection board. |
| --- | --- | --- | --- | --- |
| 34277 | BMS2 Temperature | S16 | 0.1℃ | Description: Data from Battery 2 BMS. BMS2 data is only applicable to energy storage models supporting dual batteries. |
| 34278 | BMS2 SOC | U16 | 1% | Description: From Battery 2 BMS. |
| 34279 | BMS2 SOH | U16 | 1% | Description: From Battery 2 BMS. |
| 34280 | BMS2 Charging Vol- tage Limit | U16 | 0.1V | Description: From Battery 2 BMS. |
| 34281 | BMS2 Charging Cur- rent Limit | U16 | 0.1A | Description: From Battery 2 BMS. |
| 34282 | BMS2 Discharging Current Limit | U16 | 0.1A | Description: From Battery 2 BMS. |
| 34289 | Battery 2 Real-time Voltage Value | U16 | 0.1V | Description: Battery 2 Real-time Voltage Value. Inverter Battery 2 data is only applicable to energy storage models supporting dual bat- teries. |
| 34290 | Battery 2 Real-time Current Value | S16 | 0.1A | Description: - The charge/discharge direction is determined by register 34291. - The absolute value of this regis- ter represents the real-time current value of Battery 2. |
| 34291 | Battery 2 Real-time Charge/Discharge Di- rection | U16 |  | 0: Charging 1: Discharging |
| 34328 | Smartport Phase A AC Voltage | U16 | 0.1V | Registers 34328~34333 represent the real-time voltage and current of the Smart Port (which can be con- figured as a generator, smart load, or AC coupling). |
| 34329 | Smartport Phase B AC Voltage | U16 | 0.1V |  |

| 34330 | Smartport Phase C AC Voltage | U16 | 0.1V |  |
| --- | --- | --- | --- | --- |
| 34331 | Smartport Phase A AC Current | U16 | 0.1A |  |
| 34332 | Smartport Phase B AC Current | U16 | 0.1A |  |
| 34333 | Smartport Phase C AC Current | U16 | 0.1A |  |
| 34343 | Grid-side Home Load Power (High Register) | U16 | 1W | Combined with register 33147 to form the grid-side load power. Ex- ample: Power = 700,000 W, 700,000 (Dec) = 0x00011170 (Hex). Therefore, register 34343 data is 0x0001, and register 33147 data is 0x1170. |
| 34344 | Backup Load Power (High Register) | S16 | 1W | Combined with register 33148 to form the Backup load power. Examples: - Power = 700,000 W, 700,000 (Dec) = 0x00011170 (Hex). Thus, register 34344 data is 0x0001, and register 33148 data is 0x1170. - Power = -1,000 W, -1,000 (Dec) = 0xFFFFFC18 (Hex). Thus, register 34344 data is 0xFFFF, and register 33148 data is 0xFC18. |
| 34348 | Battery 1 BMS Mini- mum Cell Voltage | U16 | 0.001V |  |
| 34349 | Battery 1 BMS Maxi- mum Cell Voltage | U16 | 0.001V |  |
| 34350 | Battery 1 BMS Mini- mum Cell Temperature | U16 | 0.1℃ |  |
| 34351 | Battery 1 BMS Maxi- mum Cell Temperature | U16 | 0.1℃ |  |
| 34367 | HMI-LCD Firmware Version | U16 |  | High Byte: Major Version Number Low Byte: Minor Version Number |
| 34368~ 34369 | Battery 2 Real-time Power Value | S32 | 1W | Description: - The charge/discharge direction is determined by register 34291. - The absolute value of this regis- ter represents the real-time power value of Battery 2. |

|  |  |  |  | (3) Applicable only to models sup- porting dual battery ports, representing the power of battery port. |
| --- | --- | --- | --- | --- |
| 34371 | BMS2 Discharge Vol- tage Limit Value | U16 | 0.1V | Description: From Battery 2 BMS. |
| 34372 | BMS2 Status | U16 |  | BIT00: Charge Disable – 0: Invalid, 1: Valid BIT01: Discharge Disable – 0: Invalid, 1: Valid BIT02: Forced Charge – 0: No Re- quest, 1: Request Forced Charge BIT04~15: Reserved |
| 34373 | BMS2 Minimum Cell Voltage | U16 | 0.001V |  |
| 34374 | BMS2 Maximum Cell Voltage | U16 | 0.001V |  |
| 34375 | BMS2 Minimum Cell Temperature | U16 | 0.1℃ |  |
| 34376 | BMS2 Maximum Cell Temperature | U16 | 0.1℃ |  |
| 34391 | Smart Port Phase A Ac- tive Power (for con- nected smart load or grid-tied inverter) | S16 | 10W | A positive value indicates power flowing out of the energy storage inverter's Smart Port, while a nega- tive value indicates power flowing into the Smart Port. |
| 34392 | Smart Port Phase B Ac- tive Power (connected smart load or grid-tied inverter) | S16 | 10W | Positive values indicate power flowing out of the energy storage inverter's Smart Port; negative val- ues indicate power flowing into the Smart Port. |
| 34393 | Smart Port Phase C Ac- tive Power (connected smart load or grid-tied inverter) | S16 | 10W | Positive values indicate power flowing out of the energy storage inverter's Smart Port; negative val- ues indicate power flowing into the Smart Port. |
| 34410 | Generator Frequency | U16 | 0.01Hz |  |
| 34411~ 34412 | Smart Load Total Power Consumption | U32 | 1kWh | For parallel systems, the data in this register of the master unit represents the total power consumption of the Smart load in the parallel system. |
| 34413 | Smart Load Daily Pow- er Consumption | U32 | 1kWh | For parallel systems, the data in this register of the master unit represents the daily power consumption of the |

|  |  |  |  | Smart load in the parallel system. |
| --- | --- | --- | --- | --- |
| 34424 | Grid-side Load Phase A Active Power | U16 | 10W | Currently only supports the S6 gen- eration of three-phase energy sto- rage machines. |
| 34425 | Grid-side Load Phase B Active Power | U16 | 10W | Currently only supports the S6 gen- eration of three-phase energy sto- rage machines. |
| 34426 | Grid-side Load Phase C Active Power | U16 | 10W | Currently only supports the S6 gen- eration of three-phase energy sto- rage machines. |
| 34427 | Parallel System Infor- mation Valid Flag | U16 |  | 0xAA55 – Parallel system power values (registers 34428~34434, 34490~34491) are valid. Any other value – invalid. |
| 34428 | Parallel System Total PV Power | S16 | 100W |  |
| 34429 | Parallel System Total Generator Active Power | S16 | 100W |  |
| 34430 | Parallel System Total Battery Power | S16 | 100W | Positive value indicates battery charging, negative value indicates battery discharging. |
| 34431 | Parallel System Total Backup Load Active Power | S16 | 100w |  |
| 34432 | Parallel System Total Inverter Active Power | S16 | 100w | Positive value indicates power flowing toward the grid, negative value indicates power being drawn from the grid. |
| 34433 | Parallel System Total Smart Load Active Power | S16 | 100w | Positive value indicates power flowing out of the Smart Port, nega- tive value indicates power flowing into the Smart Port. |
| 34434 | Parallel System AC Couple Total Active Power | S16 | 100w | Positive value indicates power flowing out of the AC Coupling port, negative value indicates power flowing into the AC Coupling port. |
| 34445~ 34446 | AC Coupling Total Power Generation | U32 | 1kWh | Indicates the energy output from the grid-tied inverter to the energy sto- rage system after the Smart Port of the energy storage inverter is confi- gured for AC Coupling functionali- ty. |
| 34451 | AC Coupling Daily Power Generation | U16 | 0.1kW h |  |

| 34490 | Parallel System Grid-side Load Total Active Power | S16 | 100W |  |
| --- | --- | --- | --- | --- |
| 34491 | Parallel System Public Grid-side Total Active Power | S16 | 100W | Positive value indicates power flowing toward the grid, negative value indicates power being drawn from the grid. |
| 34498 | PV DC Voltage 9 | U16 | 0.1V |  |
| 34499 | PV DC Current 9 | U16 | 0.1A |  |
| 34500 | PV DC Voltage 10 | U16 | 0.1V |  |
| 34501 | PV DC Current 10 | U16 | 0.1A |  |
| 34537 | Parallel System AC Grid Port Total Active Power | S16 |  | Positive value indicates power flowing out of the AC Grid port; negative value indicates power flowing into the AC Grid port. Note: Readable only by the master unit in a parallel system. |
| 34578 | Battery 2 BMS Real-time Status | U16 |  | bits 00–01: Forced charging request – 0: invalid, 1: no request, 2: re- quest, 3: invalid bits 02–03: Auxiliary heating re- quest – 0: invalid, 1: no request, 2: request, 3: invalid bits 04–15: reserved |
| 33590 | Generator Pre- heat/Cooling Operation Status | U16 |  | 1: Generator Stopped 2: Generator Supplying Power 3: Generator Preheating 4: Generator Cooling 5–65535: Invalid |
| 34600 | Module ID 1 【For each ports’ power values (For this de- vice)】 | U16 |  | 0x0001 indicates the power values of this unit's ports. Any other value is invalid. Description: - The content of Module 1 was added from a certain firmware ver- sion onwards. The conditions for use are as specified in (2). When Module 1 is invalid, relevant non‑contiguous register addresses can be read. - Criteria for Module 1 validity: - Register 34600 value equals 0x0001, - Register 34601 value is in the |

|  |  |  |  | range 1~48 (decimal), - Register 34602 value equals 0xAA55. |
| --- | --- | --- | --- | --- |
| 34601 | Module 1 Register Count | U16 |  | Low byte: Number of valid registers in 34602~34649, not exceeding 48. High byte: Reserved, default 0x00. Note: When Module 1 is active, the value of this register ranges from 1 to 48. |
| 34602 | Valid Identifier – For each ports’ power val- ues (For this device) | U16 |  | 0xAA55 – The power values of this unit's ports (registers 34603~34649) are valid. Any other value – invalid. |
| 34603~ 34604 | PV Power | S32 | 1W | Positive values are valid; negative values are invalid. 0x80000000 indicates invalid. Note: For models without a PV port (e.g., AC Coupled), this register is fixed at 0x80000000. |
| 34605~ 34606 | Battery 1 Power | S32 | 1W | Positive value indicates charging; negative value indicates discharg- ing. 0x80000000 indicates invalid. |
| 34607~ 34608 | Battery 2 Power | S32 | 1W | Positive value indicates charging; negative value indicates discharg- ing. 0x80000000 indicates invalid. Description: Only applicable to models with a Battery 2 port. For models without a Battery 2 port, this register is fixed at 0x80000000. |
| 34609~ 34610 | Inverting Bridge Total Active Power | S32 | 1W | Positive value indicates feeding power to the grid; negative value indicates drawing power from the grid. 0x80000000 indicates invalid. |
| 34611~ 34612 | Backup Load Total Ac- tive Power | S32 | 1W | Positive value indicates power flowing out of the Backup port; negative value indicates power flowing into the Backup port. 0x80000000 indicates invalid. |
| 34613~ 34614 | Backup Load Total Ap- parent Power | S32 | 1VA | Positive values are valid; negative values are invalid. 0x80000000 indicates invalid. |

| 34615~ 34616 | Inverter AC Grid Port Total Active Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates invalid. |
| --- | --- | --- | --- | --- |
| 34617~ 34618 | Generator Total Active Power | S32 | 1W | Positive values are valid; negative values are invalid. 0x80000000 indicates invalid. Note: When no generator is con- nected, this register is fixed at 0x80000000. |
| 34619~ 34620 | Smart Load Total Ac- tive Power | S32 | 1W | Positive value indicates power flowing out of the Smart port; nega- tive value indicates power flowing into the Smart port. 0x80000000 indicates invalid. Note: For models without a Smart port or when the Smart port is not configured for Smart load functio- nality, this register is fixed at 0x80000000. |
| 34621~ 34622 | Grid-tied Inverter Out- put Total Active Power | S32 | 1W | Positive values are valid; negative values are invalid. 0x80000000 indicates invalid. Note: When no grid‑tied inverter is connected, this register is fixed at 0x80000000. |
| 34623~ 34624 | Grid-side Load Total Active Power | S32 | 1W | Positive values are valid; negative values are invalid. 0x80000000 indicates invalid. |
| 34625~ 34626 | Public Grid Total Ac- tive Power | S32 | 1W | Positive value indicates feeding power to the grid; negative value indicates drawing power from the grid. 0x80000000 indicates invalid. Note: For machines without sam- pling on the public grid side, this register is fixed at 0x80000000. |
| 34799 | Remote Control (e.g., for frequency regula- tion) Protocol Version | U16 |  | High byte: Major version number Low byte: Minor version number Example: If the register value is 0x0100, it indicates the protocol version is 0100. |

|  |  |  |  | Description: - A high byte of 0x01 indicates support for Remote Control V1 protocol (starting from register 43280). |
| --- | --- | --- | --- | --- |
| 34900 | Module ID 6 【 For hybrid system with PV and hybrid inverters】 | U16 |  | 0x0006 — Photovoltaic & Storage System Information Any other value is invalid. Description: - The content of Module 6 was added starting from a specific firmware version. Usage conditions are as described in (2). When Mod- ule 6 is invalid, some information can be read from relevant non‑contiguous register addresses. - Criteria for Module 6 validity: - Register 34900 value equals 0x0006, - Register 34901 value is in the range 1~48 (decimal), - Register 34902 value equals 0xAA55. |
| 34901 | Module 6 Register Count | U16 |  | Low byte: Number of valid registers in the range 34902~34949, not ex- ceeding 48. High byte: Reserved, default 0x00. Note: When Module 6 is active, the value of this register ranges from 1 to 48. |
| 34902 | Valid Identifier - For hybrid system with PV and hybrid inverters | U16 |  | 0xAA55–Photovoltaic & Storage System Information (registers 34903~34949) is valid. Any other value – invalid. |
| 34903~ 34904 | Hybrid inverters’ PV Total Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates the value is invalid. Description: Represents the cumu- lative PV power connected to all energy storage units in the system. |

| 34905~ 34906 | Hybrid inverters’ To- tal Battery Power | S32 | 1W | Positive value indicates battery charging; negative value indicates battery discharging. 0x80000000 indicates the value is invalid. Description: Represents the cumu- lative battery power connected to all energy storage units in the system. |
| --- | --- | --- | --- | --- |
| 34907~ 34908 | Hybrid inverters’ To- tal Inverter Active Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates the value is invalid. Description: Represents the cumu- lative inverter power of all energy storage units in the system. |
| 34909~ 34910 | System Backup Load Total Active Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates the value is invalid. Description: Represents the cumu- lative power of the system Backup load. |
| 34911~ 34912 | Hybrid inverters’ AC Grid Port Total Active Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates the value is invalid. Description: Represents the cumu- lative AC Grid port power of all energy storage units in the system. |
| 34913~ 34914 | Generator Total Active Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates the value is |

|  |  |  |  | invalid. |
| --- | --- | --- | --- | --- |
| 34915~ 34916 | Hybrid inverters’ Smart Load Total Ac- tive Power | S32 | 1W | Positive value indicates power flowing out of the Smart Port; nega- tive value indicates power flowing into the Smart Port. 0x80000000 indicates the value is invalid. Description: Represents the cumu- lative power of the system smart load. |
| 34917~ 34918 | Grid‑tied Inverters’ To- tal Active Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates the value is invalid. Description: Represents the cumu- lative power of all grid‑tied inver- ters in the system. |
| 34919~ 34920 | System Grid-side Load Total Active Power | S32 | 1W | Positive value indicates power flowing out of the energy storage inverter; negative value indicates power flowing into the energy sto- rage inverter. 0x80000000 indicates the value is invalid. |
| 34921~ 34922 | System Public Grid-side Total Active Power | S32 | 1W | Positive value indicates power flowing toward the grid; negative value indicates power being drawn from the grid. 0x80000000 indicates the value is invalid. |
| 34923 | Number of Grid-tied Inverters Online | U16 |  | Range: 0~20, other values are invalid. |
| 25000 | Module ID 7 【Remote Control In- formation】 | U16 |  | 0x0007 – Remote Control Infor- mation Any other value – invalid. Description: - The content of Module 7 is used for operational information of the Remote Control V1 function. - Criteria for Module 7 validity: - Register 25000 value equals |

|  |  |  |  | 0x0007, - Register 25001 value is in the range 1~98 (decimal), - Register 25002 value equals 0xAA55. |
| --- | --- | --- | --- | --- |
| 25001 | Module 7 Register Count | U16 |  | Low byte: Number of valid registers in the range 25002–25099, range 2~98. High byte: Reserved, default 0x00. |
| 25002 | Valid Identifier – For Remote Control Infor- mation | U16 |  | 0xAA55 – Remote Control Infor- mation (registers 25003~25099) is valid. Any other value – invalid. |
| 25003 | Remote Control Status | U16 |  | BIT00: - unready for Remote Control - ready for Remote Control BIT01: - available remote control power is not limited by BMS - available remote control power is limited by BMS BIT02: - available remote control power is not limited by inverter - available remote control power is limited by inverter BIT03: - available remote control power is not limited by grid frequency(grid code) - available remote control power is limited by grid frequency(grid code) BIT04: - available remote control power is not limited by grid voltage(grid code) - available remote control power is limited by grid voltage(grid code) BIT05: - available remote control power is not limited by active power Ramp-up(grid code) - available remote control power is limited by active power |

|  |  |  |  | Ramp-up(grid code) BIT06: - available remote control power is not limited by DRM(set by custom- er) - available remote control power is limited by DRM(set by customer) BIT07: - available remote control power is not limited by EPM(set by custom- er) - available remote control power is limited by EPM(set by customer) BIT08: - available remote control power is not limited by grid peak power(set by customer) - available remote control power is limited by grid peak power(set by customer) BIT09: - available remote control power is not limited by reactive power(set by customer) - available remote control power is limited by reactive power(set by customer) BIT10~BIT15 reserved |
| --- | --- | --- | --- | --- |
| 25004~ 25005 | This device’s Battery Available Charge Power Value | U32 | 1W |  |
| 25006~ 25007 | This device’s Battery Available Discharge Power Value | U32 | 1W |  |
| 25008~ 25009 | This device’s AC Grid Port Available Import Active Power Value | U32 | 1W |  |
| 25010~ 25011 | This device’s AC Grid Port Available Export Active Power Value | U32 | 1W |  |
| 25012~ 25013 | Parallel System Battery Available Charge Power Value | U32 | 1W |  |
| 25014~ | Parallel System Battery | U32 | 1W |  |

| 25015 | Available Discharge Power Value |  |  |  |
| --- | --- | --- | --- | --- |
| 25016~ 25017 | Parallel System AC Grid Port Available Import Active Power Value | U32 | 1W |  |
| 25018~ 25019 | Parallel System AC Grid Port Available Export Active Power Value | U32 | 1W |  |

  - Definition of Set Parameter Addresses

Corresponding function codes 0x03, 0x06, and 0x10.

| Register Address (Decimal) | Description | Data Type | Unit | Remarks |
| --- | --- | --- | --- | --- |
| 43000 | Real-Time Clock: Year | U16 |  | Range: 0~99, representing the years 2000~2099. |
| 43001 | Real-Time Clock: Month | U16 |  | Range: 1~12， representing month 1~12 |
| 43002 | Real-Time Clock: Day | U16 |  | Range: 1–31, representing day 1–31 |
| 43003 | Real-Time Clock: Hour | U16 |  | Range: 0–23, representing hour 0–23 |
| 43004 | Real-Time Clock: Minute | U16 |  | Range: 0–59, representing minute 0–59 |
| 43005 | Real-Time Clock: Second | U16 |  | Range: 0–59, representing second 0–59 |
| 43006 | Slave Address Setting | U16 |  | Setting range: 1–10, default 1. Note: Only set using function code 0x06. |
| 43007 | Startup/Shutdown | U16 |  | 0xBE–Startup , 0xDE–Shutdown |
| 43009 | Current Battery Model | U16 |  | Low byte: Low-voltage battery manufacturer (see Appendix 5 for low-voltage battery codes) High byte: High-voltage battery manufacturer (see Appendix 6 for high-voltage battery codes) |
| 43010 | Maximum Charging SOC | U16 | 1% | Setting range: 80–100%, default 100%. Note: Represents the charge cutoff SOC for communication-capable lithium batteries. |
| 43011 | Over-Discharge SOC | U16 | 1% | Setting range: 5–40%, default 20%; must be greater than the forced charge SOC (register address 43018). |
| 43018 | Forced Charge SOC | U16 | 1% | Setting range: 4% – (Over-Discharge SOC – 1%), de- fault 10% (Note: Over-Discharge SOC register address 43011). |
| 43019 | Rated Capacity | U16 | 1 Ah | Range: 0–9999 Ah, default 200 Ah. Note: Supports lead-acid and 48/51.2V non‑communication li- |

|  |  |  |  | thium batteries. |
| --- | --- | --- | --- | --- |
| 43020 | Over-Discharge Voltage | U16 | 0.1V | Lead‑acid battery: S5 models, range 40.0–48.0 V, default 44.5 V; S6 models, range 40.0–52.0 V, default 44.5 V. 48V lithium battery: range 45–52 V, default 47 V. 51.2V lithium battery: range 45–52 V, default 50 V. |
| 43021 | Forced Charge Voltage | U16 | 0.1V | Lead‑acid battery: S5 models, range 40.0–48.0 V, default 43.8 V; S6 models, range 40.0–50.0 V, default 43.8 V. |
| 43022 | Lead‑Acid Battery Temperature Compen- sation Coefficient | U16 | 1mV/ ℃ | Range: 0–180 mV/°C, Default: 0 mV/°C; Note: Only supported for lead‑acid batteries. |
| 43023 | Ambient Temperature Status Selection | U16 |  | 1: Normal Temperature, 2: Low Temperature, 3: High Tempera- ture,Other values invalid; Default: 1; Note: Only supported for lead‑acid batteries. |
| 43024 | Battery Reserved SOC | U16 | 1% | Range: Over-discharge SOC to 100%, default 80% (Note: Over-discharge SOC register 43011) Description: Parameter setting for enabling backup battery functional- ity. |
| 43038 | 81>S1 | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. Note: Registers 43038-43049 are only effective when configured un- der the CEI 0-21 standard. |
| 43039 | 81>S1-T | U16 | 0.01s | The configurable range and default values are determined according to the national standard parameter table. |
| 43040 | 81<S1 | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter |

|  |  |  |  | table. |
| --- | --- | --- | --- | --- |
| 43041 | 81<S1-T | U16 | 0.01s | The configurable range and default values are determined according to the national standard parameter table. |
| 43042 | 81>S2F | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43043 | 81>S2F-T | U16 | 0.01s | The configurable range and default values are determined according to the national standard parameter table. |
| 43044 | 81<S2F | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43045 | 81<S2F-T | U16 | 0.01s | The configurable range and default values are determined according to the national standard parameter table. |
| 43046 | 81>S2S | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43047 | 81>S2S-T | U16 | 0.01s | The configurable range and default values are determined according to the national standard parameter table. |
| 43048 | 81<S2S | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43049 | 81<S2S-T | U16 | 0.01s | The configurable range and default values are determined according to the national standard parameter table. |
| 43068 | National Standard Number | U16 |  | Refer to Appendix 2. |
| 43071 | Built-in EPM Hard lim- it Switch (Note: Related to the Australian 2020 new standard) | U16 |  | 00: Default invalid action com- mand; 01: Turn On; 02: Turn Off; Applicable to all series covered by |

|  |  |  |  | the Australian new standard. (Note: Related to the Australian 2020 new standard) |
| --- | --- | --- | --- | --- |
| 43072 | Built-in EPM Hard lim- it Backflow power val- ue (Note: Related to Australian 2020 new standard) | S16 | 100W | Standalone setting range: 0–1.1 times inverter rated power. Parallel setting range: 0–1.1 times inverter rated power × number of units. Setting method V2 range: Standalone: 0–4 times inverter rated power, default: 1.1 times inverter rated power. Parallel: 0–4 times inverter rated power × number of units, default: 1.1 times inverter rated power × number of units. Positive value indicates power fed to the grid; negative value indicates power drawn from the grid. (Note: Related to Australian 2020 new standard) |
| 43073 | Meter/CT Placement Setting | U16 |  | BIT00–03: Reserved BIT04: EPM switch (an- ti‑reverse‑flow power setting switch), 0–Off, 1–On, default 0. (Note: Related to Australian 2020 new standard, EPM soft switch) BIT05: FailSafe switch, 0–Off, 1–On, default 0. BIT06: Power control mode, de- fault 0; 0: Three‑phase unified control (in- verter outputs balanced current); 1: Three‑phase independent control (inverter outputs unbalanced cur- rent). BIT07–12: Reserved BIT13: Meter/CT selection for pub- lic grid‑side energy management, 0–Meter, 1–CT; default 0 (applies to energy storage machines sup- porting both Meter and CT). BIT14: Control mode for sin- |

|  |  |  |  | gle‑phase energy storage machine connected to a three‑phase meter, 0–Total power, 1–Single‑phase power, default 0 (for S6‑generation energy storage machines). BIT15: Reserved |
| --- | --- | --- | --- | --- |
| 43074 | EPM Backflow Power Setting | S16 | 100W | RHI-(3-6)K-48ES-5G：1<-->100W, Setting range: 0~99. RHI-1P(5-10)K-HVES-5G/RHI-3P (5-10)K-HVES-5G/RAI-3K-48ES- 5G：1<-->1W, Setting range: 0~30000. S6 Models：1<-->100W, Standalone/Three‑Phase Network: Setting range: 0–1.1 times inverter rated power. Parallel System: Setting range: 0–1.1 times inverter rated power × number of units. Setting method V2 range: Standalone: 0–4 times inverter rated power, default: 1.1 times inverter rated power. Parallel: 0–4 times inverter rated power × number of units, default: 1.1 times inverter rated power × number of units. Upper limit uniformly set to 3 MW (related to register 34806 bits 06–07). (Note: Related to Australian 2020 new standard, EPM soft backflow power limit.) |
| 43076 | AFCI Turn On / Turn Off | U16 |  | 1<--> Turn On 0<--> Turn Off |
| 43077 | Italian Standard Mode Switching Digital Sig- nal | U16 |  | 0: Off (default: off) (81>S1 – 50.2 Hz / 0.1 s – Inverter 81<S1 – 49.8 Hz / 0.1 s – Inverter) 1: Local Control (81>S2 – 51.5 Hz / 0.1 s – Local 81<S2 – 47.5 Hz / 0.1 s – Local) 2: External Signal (81>S2 – 51.5 Hz / 1.0 s – External |

|  |  |  |  | 81<S2 – 47.5 Hz / 4.0 s – External) Note: Settings are non‑volatile and can only be configured under the Italian CEI 0‑21 standard. |
| --- | --- | --- | --- | --- |
| 43079 | One‑Key Full Test (Complete Italian Self‑check Items 01‑10) | U16 |  | Value: Start Complete Self Test 0---One‑key full test stopped or not started 2---One‑key full test started |
| 43082 | Grid Upper Voltage Limit Required for Post‑Fault Recovery | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. |
| 43083 | Grid Lower Voltage Limit Required for Post‑Fault Recovery | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. |
| 43084 | Grid Upper Frequency Limit Required for Post‑Fault Recovery | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43085 | Grid Lower Frequency Limit Required for Post‑Fault Recovery | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43086 | Grid Upper Voltage Limit Required for First Power‑On | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. |
| 43087 | Grid Lower Voltage Limit Required for First Power‑On | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. |
| 43088 | Grid Upper Frequency Limit Required for First Power‑On | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43089 | Grid Lower Frequency Limit Required for First Power‑On | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43090 | Grid Primary Over‑Voltage Threshold | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. |

|  |  |  |  | For the CEI 0‑21 standard, it represents 59 Hz S2. |
| --- | --- | --- | --- | --- |
| 43091 | Grid Primary Over‑Voltage Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. For the CEI 0‑21 standard, it represents 59.S2 Time |
| 43092 | Grid Secondary Over‑Voltage Threshold | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. |
| 43093 | Grid Secondary Over‑Voltage Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. |
| 43094 | Grid Primary Un- der‑Voltage Threshold | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. For the CEI 0‑21 standard, it represents 27.S1 |
| 43095 | Grid Primary Un- der‑Voltage Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. For the CEI 0‑21 standard, it represents 27.S1 Time |
| 43096 | Grid Secondary Un- der‑Voltage Threshold | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. For the CEI 0‑21 standard, it represents 27.S2 |
| 43097 | Grid Secondary Un- der‑Voltage Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. For the CEI 0‑21 standard, it represents 27.S2 Time |
| 43098 | Grid Primary Over‑Frequency Thre- shold | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |

| 43099 | Grid Primary Over‑Frequency Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. For the Hawaiian and new U.S. standard UL1547‑2018,1<-->20mS (Reason: Since the upper limit of the parameter range is 1000 s, if 1<-->10mS，the maximum value of a single register would be 655.35 s, which does not meet the safety reg- ulation requirements.) |
| --- | --- | --- | --- | --- |
| 43100 | Grid Secondary Over‑Frequency Thre- shold | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43101 | Grid Secondary Over‑Frequency Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. For the Hawaiian and new U.S. standard UL1547‑2018,1<-->20mS |
| 43102 | Grid Primary Un- der‑Frequency Thre- shold | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43103 | Grid Primary Un- der‑Frequency Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. For the Hawaiian and new U.S. standard UL1547‑2018, 1<-->20 ms. |
| 43104 | Grid Secondary Un- der‑Frequency Thre- shold | U16 | 0.01Hz | The configurable range and default values are determined according to the national standard parameter table. |
| 43105 | Grid Secondary Un- der‑Frequency Delay Threshold | U16 | 10ms | The configurable range and default values are determined according to the national standard parameter table. For the Hawaiian and new U.S. standard UL1547‑2018, 1<-->20 ms. |

| 43106 | Start‑up Time | U16 | 1s | The configurable range and default values are determined according to the national standard parameter table. |
| --- | --- | --- | --- | --- |
| 43107 | Fault Recovery Time | U16 | 1s | The configurable range and default values are determined according to the national standard parameter table. |
| 43108 | 10‑Minute Average Over‑Voltage Protection Threshold | U16 | 0.1V | The configurable range and default values are determined according to the national standard parameter table. For the CEI 0‑21 standard, it represents 59 Hz S1. |
| 43110 | Energy Storage Control Switch | U16 |  | For details, refer to Appendix 7: Energy Storage Control Switch Status Description. Note: BIT00 (Self‑Consumption Priority), BIT06 (Grid Feed‑in Priority), and BIT11 (Peak‑Shaving) cannot be enabled simultaneously. BIT04 (Backup Battery Enable) and BIT11 (Peak‑Shaving) cannot be enabled simultaneously. Operation Instructions for Writing BITxx: The host computer shall first read the current value of this register, then modify the value of the corresponding BIT as needed based on the current value, and fi- nally write the updated value back. |
| 43111 | Backup Load Function Enable Setting | U16 |  | 0000H – Disabled, 0001H – Enabled, default: Enabled. |
| 43112 | Backup Port AC Output Voltage Setting | U16 | 0.1V | Standard Voltage Grid: Phase vol- tage range: 190–250 V; Default: 230 V. Low Voltage Grid: Phase voltage range: 110–140 V, Default: 132 V; Line voltage range: 190–250 V, Default: 230 V. |
| 43117 | Battery 1 Maximum Charging Current Set- ting | U16 | 0.1A | 5G Series: Range: 1–100 A, De- fault: 100 A. S5 Series: Range: 1 – unit's battery |

|  |  |  |  | maximum charging current, De- fault: unit's battery maximum charging current. S6 Series: Range: 0 – unit's battery maximum charging current, De- fault: unit's battery maximum charging current. |
| --- | --- | --- | --- | --- |
| 43118 | Battery 1 Maximum Discharging Current Setting | U16 | 0.1A | 5G Series: Range: 1–100 A, De- fault: 100 A. S5 Series: Range: 1 – unit's battery maximum discharging current, De- fault: unit's battery maximum dis- charging current. S6 Series: Range: 0 – unit's battery maximum discharging current, De- fault: unit's battery maximum dis- charging current. |
| 43123 | Overload Voltage Droop Setting | U16 |  | 0000H – Disabled, 0001H – Enabled, default: Disabled. |
| 43125 | Phase A Reverse Power Flow Setting | S16 | 100W | Range: 0–99, default 0. Effective only when BIT06 (power control mode) of register 43073 is set to "three‑phase unbalanced out- put". Note: Only applicable to S6 three‑phase high‑voltage 10 kW series and S6 single‑phase high‑voltage 11.4 kW series soft- ware versions that have not been simplified; corresponds to register 35000 values 0x2070 and 0x2080. |
| 43126 | Phase B Reverse Power Flow Setting | S16 | 100W | 1<-->100W，Range: 0–99, default 0. Effective only when BIT06 (power control mode) of register 43073 is set to "three‑phase unbalanced out- put". Note: Only applicable to S6 three‑phase high‑voltage 10 kW series and S6 single‑phase high‑voltage 11.4 kW series soft- ware versions that have not been simplified; corresponds to register 35000 values 0x2070 and 0x2080. |

| 43127 | Phase C Reverse Power Flow Setting | S16 | 100W | 1<-->100W，Range: 0–99, default 0. Effective only when BIT06 (power control mode) of register 43073 is set to "three‑phase unbalanced out- put". Note: Only applicable to S6 three‑phase high‑voltage 10 kW series software versions that have not been simplified; corresponds to register 35000 value 0x2070. |
| --- | --- | --- | --- | --- |
| 43128 | Remote Control: Inver- ter AC Grid Port Active Power Setting | S16 | 10W | Range：0~300kW Positive value indicates power flowing out of the inverter; negative value indicates power flowing into the inverter. Description: - Effective only after remote con- trol of the inverter AC Grid port is enabled (register 43132 = 2). - Settings are not retained after power loss. |
| 43129 | Remote Control: Bat- tery Discharging Power Setting | U16 | 10W | Range：0~300kW Description: - Effective only after remote con- trol of battery discharging is enabled (register 43135 = 2). - Settings are not retained after power loss. |
| 43130 | Remote Control: Bat- tery Charging Limit Power | U16 | 10W | Range: 10 W – device Backup rated output power; default 0 (invalid). Note: Settings are not retained after power loss. |
| 43131 | Remote Control: Bat- tery Discharging Limit Power | U16 | 10W | Range: 10 W – device Backup rated output power; default 0 (invalid). Note: Settings are not retained after power loss. |
| 43132 | Remote Control: Grid Regulation via Remote Control | U16 |  | 0: Off 1: Reserved 2: Enable remote control of inverter AC Grid port (active power setting register 43128) 3–65535: Reserved If no continuous "enable" command |

|  |  |  |  | is received within 5 minutes after an enable command is received, the function will automatically turn off. When this function is enabled, if remote control of battery charg- ing/discharging was previously ac- tive, remote control of forced bat- tery charging will automatically stop. Description: - Command timeout period: de- fault 5 minutes. After setting the timeout period in register 43282, operation follows the set timeout value. - Settings are not retained after power loss. |
| --- | --- | --- | --- | --- |
| 43135 | Remote Control: Bat- tery Charge/Discharge Mode Setting | U16 |  | 0: Off 1: Battery Charging 2: Battery Discharging 3–65535: Reserved Description: - When this function is enabled, if remote grid regulation control was previously active, the remote grid regulation mode will automatically stop. - Settings are not retained after power loss. |
| 43136 | Remote Control: Bat- tery Charging Power Setting | U16 | 10W | Range: 0–300 kW Description: - Effective only after remote con- trol of battery charging is enabled (register 43135 = 1). - Settings are not retained after power loss. |
| 43139 | EPS Switchover Time | U16 | 10ms | Host computer setting range: 1–500 s; default: 2000 ms. Note: Before the addition of regis- ter 43705, setting register 43139 to 0 meant the EPS control function was turned off. After the addition of register 43705, register 43139 can- not be set to 0. |

| 43140 | Meter Type and Its In- stallation Location | U16 |  | High byte indicates meter installa- tion location: 0x0100 – Grid side 0x0200 – Reserved 0x0300 – Grid side + parallel in- verter output side (dual meters) Note: Applicable to Eastron stan- dard single‑phase, Eastron standard three‑phase, and Chint dual‑channel meters. Low byte indicates meter type: 0x0001 – Acrel single‑phase 0x0002 – Acrel three‑phase 0x0003 – Reserved 0x0004 – Eastron standard sin- gle‑phase 0x0005 – Eastron standard three‑phase 0x0006 – No meter mode 0x0007 – Chint split‑phase meter 0x0008 – Chint dual‑channel meter |
| --- | --- | --- | --- | --- |
| 43141 | TOU Scheduled Charg- ing Current Setting | U16 | 0.1A | Range: 0 – maximum rated charg- ing current of the corresponding model, default 50 A. Description: - Only used for parameter settings in Optimization Revenue V1 ver- sion. - Takes effect when BIT01 of register 43110 is enabled. |
| 43142 | TOU Scheduled Dis- charging Current Set- ting | U16 | 0.1A | Range: 0 – maximum rated dis- charging current of the correspond- ing model, default 50 A. |
| 43143 | TOU Scheduled Charg- ing Start Hour Setting | U16 | hour | 1<-->1h |
| 43144 | TOU Scheduled Charg- ing Start Minute Setting | U16 | min | 1<-->1m |
| 43145 | TOU Scheduled Charg- ing End Hour Setting | U16 | hour | 1<-->1h |
| 43146 | TOU Scheduled Charg- ing End Minute Setting | U16 | min | 1<-->1m |
| 43147 | TOU Scheduled Dis- charging Start Hour Setting | U16 | hour | 1<-->1h |

| 43148 | TOU Scheduled Dis- charging Start Minute Setting | U16 | min | 1<-->1m |
| --- | --- | --- | --- | --- |
| 43149 | TOU Scheduled Dis- charging End Hour Set- ting | U16 | hour | 1<-->1h |
| 43150 | TOU Scheduled Dis- charging End Minute Setting | U16 | min | 1<-->1m |
| 43153 | TOU Scheduled Charg- ing Start Hour Setting 2 | U16 | hour | 1<-->1h |
| 43154 | TOU Scheduled Charg- ing Start Minute Setting 2 | U16 | min | 1<-->1m |
| 43155 | TOU Scheduled Charg- ing End Hour Setting 2 | U16 | hour | 1<-->1h |
| 43156 | TOU Scheduled Charg- ing End Minute Setting 2 | U16 | min | 1<-->1m |
| 43157 | TOU Scheduled Dis- charging Start Hour Setting 2 | U16 | hour | 1<-->1h |
| 43158 | TOU Scheduled Dis- charging Start Minute Setting 2 | U16 | min | 1<-->1m |
| 43159 | TOU Scheduled Dis- charging End Hour Set- ting 2 | U16 | hour | 1<-->1h |
| 43160 | TOU Scheduled Dis- charging End Minute Setting 2 | U16 | min | 1<-->1m |
| 43163 | TOU Scheduled Charg- ing Start Hour Setting 3 | U16 | hour | 1<-->1h |
| 43164 | TOU Scheduled Charg- ing Start Minute Setting 3 | U16 | min | 1<-->1m |
| 43165 | TOU Scheduled Charg- ing End Hour Setting 3 | U16 | hour | 1<-->1h |
| 43166 | TOU Scheduled Charg- ing End Minute Setting 3 | U16 | min | 1<-->1m |
| 43167 | TOU Scheduled Dis- charging Start Hour Setting 3 | U16 | hour | 1<-->1h |

| 43168 | TOU Scheduled Dis- charging Start Minute Setting 3 | U16 | min | 1<-->1m |
| --- | --- | --- | --- | --- |
| 43169 | TOU Scheduled Dis- charging End Hour Set- ting 3 | U16 | hour | 1<-->1h |
| 43170 | TOU Scheduled Dis- charging End Minute Setting 3 | U16 | min | 1<-->1m |
| 43173 | TOU Scheduled Charg- ing Start Hour Setting 4 | U16 | hour | 1<-->1h |
| 43174 | TOU Scheduled Charg- ing Start Minute Setting 4 | U16 | min | 1<-->1m |
| 43175 | TOU Scheduled Charg- ing End Hour Setting 4 | U16 | hour | 1<-->1h |
| 43176 | TOU Scheduled Charg- ing End Minute Setting 4 | U16 | min | 1<-->1m |
| 43177 | TOU Scheduled Dis- charging Start Hour Setting 4 | U16 | hour | 1<-->1h |
| 43178 | TOU Scheduled Dis- charging Start Minute Setting 4 | U16 | min | 1<-->1m |
| 43179 | TOU Scheduled Dis- charging End Hour Set- ting 4 | U16 | hour | 1<-->1h |
| 43180 | TOU Scheduled Dis- charging End Minute Setting 4 | U16 | min | 1<-->1m |
| 43183 | TOU Scheduled Charg- ing Start Hour Setting 5 | U16 | hour | 1<-->1h |
| 43184 | TOU Scheduled Charg- ing Start Minute Setting 5 | U16 | min | 1<-->1m |
| 43185 | TOU Scheduled Charg- ing End Hour Setting 5 | U16 | hour | 1<-->1h |
| 43186 | TOU Scheduled Charg- ing End Minute Setting 5 | U16 | min | 1<-->1m |
| 43187 | TOU Scheduled Dis- charging Start Hour Setting 5 | U16 | hour | 1<-->1h |

| 43188 | TOU Scheduled Dis- charging Start Minute Setting 5 | U16 | min | 1<-->1m |
| --- | --- | --- | --- | --- |
| 43189 | TOU Scheduled Dis- charging End Hour Set- ting | U16 | hour | 1<-->1h |
| 43190 | TOU Scheduled Dis- charging End Minute Setting 5 | U16 | min | 1<-->1m |
| 43195 | Total Grid‑side Active Power Control Com- pensation | S16 | 1W | Range: For units with rated power ≤ 20 kW: –1000 W to +1000 W For units with rated power > 20 kW: –10 kW to +10 kW Default: –30 W |
| 43279 | Remote Control: Func- tion Switch | U16 |  | BIT00–BIT01: PV Shutdown con- trol – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT02–BIT15: Reserved. Description: - Effective only when remote battery charge/discharge control (register 43135) or remote AC con- trol (register 43132) mode is active. - While remote control mode is active, if an invalid value is written to any switch setting (enabled or disabled), the corresponding regis- ter bit data will revert to its pre- vious enabled/disabled state, en- suring that a valid data status can be read for each switch setting. - After remote control mode is exited, this register data is cleared to 0. - Settings are not retained after power loss. |
| 43282 | Remote Control: Time- out Setting | U16 | 1min | Range: 2–30; default 5. Note: Settings are not retained after power loss. |
| 43283 | Meter Communication Access Method | U16 |  | 0 – Wired, 1 – Wireless; other val- ues invalid, default 0. |
| 43284 | Special Function Con- trol Word 02 | U16 |  | BIT00: PV‑Only Load Enable – 0: disabled, 1: enabled, default 0. |

|  |  |  |  | BIT01: Fan Low‑Noise Mode – 0: disabled, 1: enabled, default 0. BIT02: Battery Saving – 0: enabled, 1: disabled, default 0. BIT03–15: Reserved. |
| --- | --- | --- | --- | --- |
| 43285 | AC Coupling Start SOC | U16 | 1 | Range: 0 to (AC Coupling Stop SOC – 10%), default 0. Only applicable to battery types with communication capability. |
| 43286 | AC Coupling Start Vol- tage | U16 | 0.1V | Range: Over‑discharge voltage to (AC Coupling Stop Voltage – 2 V), default 48 V. Only applicable to battery types without communication capability. |
| 43287 | AC Coupling Start Frequency | U16 | 0.01Hz | 50 Hz Standard: 50 Hz ~ (primary over‑frequency threshold + 0.1 Hz), default 50 Hz. 60 Hz Standard: 60 Hz ~ (primary over‑frequency threshold + 0.1 Hz), default 60 Hz. |
| 43300 | G100‑2022 Standard Public Grid‑side Ap- parent Current Output Limit Setting | U16 | 0.01A | For three‑phase energy storage machines, this indicates the appar- ent current output limit per phase. Standalone range: 0 ~ 4 × unit rated AC output current. Parallel system range: 0 ~ 4 × unit rated AC output current × number of parallel units. Note: The set upper limit must not exceed the data‑type upper limit of this register. |
| 43313 | Clear AFCI Fault | U16 |  | Used to manually clear the fault after 5 cumulative AFCI faults have occurred on the same day. 0xAA55 – enable, other values invalid. Only writable via single‑register command 0x06. |
| 43333 | Lead‑Acid Battery Equalization Enable | U16 |  | 0: Disable; 1: Enable. Default: 0. |
| 43334 | Lead‑Acid Battery Equalization Voltage | U16 | 0.1V | Range: 55–59.5 V; default 57.6 V. |
| 43335 | Lead‑Acid Battery Equalization Time | U16 | 1min | Range: 120–360 min; default 180 min. |

| 43336 | Lead‑Acid Battery Equalization Timeout | U16 | 1min | Range: 5–900 min; default 120 min. |
| --- | --- | --- | --- | --- |
| 43337 | Lead‑Acid Battery Equalization Interval | U16 | 1 day | Range: 20–180 days; default 30 days. |
| 43338 | Lead‑Acid Battery Equalization Immediate Activation | U16 |  | 0: Disable, 1: Enable; default 0. Requires battery equalization ena- ble to be turned on first. |
| 43339 | Lead‑Acid Battery Float Current Limit | U16 | 0.1A | Range: 4.0–10.0 A; default 4.0 A. |
| 43340 | Generator Setting Ena- ble Switch | U16 |  | BIT00: Generator connection mode – 0: Manual, 1: Automatic; default 0. BIT01: Generator charging enable – 0: Enable, 1: Disable; default 0. BIT02–15: Reserved. |
| 43344 | Generator Start Lithium Battery SOC | U16 | 1% | In generator mode, the SOC at which the generator starts and charges the lithium battery. Range: 1–95%; default 25%. |
| 43345 | Generator Lithium Bat- tery Charge Cut‑off SOC | U16 | 1% | Range: (Start SOC + 5%) – 100%; default 80%. Note: Start SOC < Cut‑off SOC. |
| 43346 | Generator Start Lead‑Acid Battery Vol- tage | U16 | 0.1V | Range: 40–55 V; default 46 V. |
| 43347 | Generator Lead‑Acid Battery Charge Cut‑off Voltage | U16 | 0.1V | Range: (Start voltage + 2 V) – 60 V; default 55 V. |
| 43348 | Battery Wake‑up Vol- tage Setting | U16 | 0.1V | Low‑voltage energy storage unit: 40–60 V, default 40 V. Off‑grid energy storage unit: 40–58 V, de- fault 40 V. Single‑phase high‑voltage energy storage unit: 120–500 V, default 120 V. Three‑phase high‑voltage energy storage unit: 120–600 V, default 120 V. Note: Registers 43348‑43349 only take effect when BIT03 of register 43110 (battery wake‑up trigger ac- tion) is enabled. |
| 43349 | Battery Wake-up Time Setting | U16 | 1s | Range: 20–3600 s, default: 20 s |
| 43361 | MPPT Active Scanning | U16 | 1s | Range: 600–10800 (10 min–180 |

|  | Interval |  |  | min); default: 1800 (30 min) |
| --- | --- | --- | --- | --- |
| 43362 | CT Ratio | U16 |  | Range: 1–30000. Note: (1) Effective only when BIT13 of register 43073 is set to CT. (2) For 50 kW, 100 kW commer- cial/industrial storage series, used for setting the CT ratio of Meter 1. |
| 43363 | Generator Start/Stop in Manual Mode | U16 |  | - Before simplified setting: Forced generator start – 0: invalid, 1: valid; default 0; other values invalid. After a single write of “1”, the inverter immediately starts the generator. When the generator stop condition is met, this register data is automatically cleared to 0. - After simplified setting: Gene- rator start/stop in manual mode – 1: start, 0: stop; default 0; other values invalid. |
| 43364 | Generator Rated Input Power | U16 | 0.1kW |  |
| 43365 | Generator Setting Switch | U16 |  | BIT00: Generator connection loca- tion – 0: generator port, 1: grid port; default 0. BIT01: With Generator – 0: No, 1: Yes; default 0. Note: Cannot be enabled simulta- neously with AC Coupling enable (register 43483 BIT01); otherwise invalid – one must be turned off before the other is turned on. BIT02: Generator enable signal – 0: disabled, 1: enabled; default 0. BIT03: AC Coupling connection location – 0: generator port, 1: Backup port; default 0. BIT04: Generator connection loca- tion (used in combination with BIT00): BIT04 = 0, BIT00 = 0: generator port (Smart port) (supported by models with Smart port) BIT04 = 0, BIT00 = 1: grid side |

|  |  |  |  | BIT04 = 1, BIT00 = 0: Backup side (currently only supported for models without a dedicated gene- rator port) BIT04 = 1, BIT00 = 1: invalid BIT05: Disabled. BIT06–15: Reserved. Operation instructions for writing BITxx: The host computer shall first read the current value of this register, then modify the value of the corresponding BIT as needed based on the current value, and fi- nally write the updated value back. |
| --- | --- | --- | --- | --- |
| 43366 | Forced Stop Generator | U16 |  | - Before simplified setting: Forced stop generator – 0: invalid, 1: valid; default 0; other values invalid. When the generator is running, a single write of “1” to this register will cause the inverter to stop the generator immediately. - After simplified setting: Deactivate. |
| 43367 | Generator Maximum Allowable Percentage | U16 | 1% | Gen_Max_Run_Pct; Range: 1%–120%, default: 100%. |
| 43368 | Generator Target Power | U16 | 0.1kW | Gen_Target_Power， Default: 90% of generator rated input power. |
| 43369 | Generator Charging Power | U16 | 0.1kW | Range: 0 – maximum charging power of the corresponding model, default 0. |
| 43374 | Function Setting Enable Switch | U16 |  | BIT00: AC Output Control Switch 0: Disable, 1: Enable; default: Disable. When Enable is selected, the inverter, upon detecting grid pres- ence, forcibly (regardless of the Backup enable switch) stops Back- up‑side output; upon detecting grid absence, it forcibly (regardless of the Backup enable switch) turns on Backup‑side output. |

|  |  |  |  | When Disable is selected, Backup output is controlled ac- cording to the Backup enable switch and the off‑grid battery over‑discharge logic. BIT01: Battery Auto‑Wake‑up Switch 0: Disable, 1: Enable; default: Disable. When set to Enable, if the in- verter does not detect battery vol- tage after power‑on, it executes a wake‑up action for the duration specified in register 43376. BIT02: Reserved BIT03: Digital Control Signal Switch – 0: OFF, 1: ON; default: 0 BIT04: Analog Control Signal Switch – 0: OFF, 1: ON; default: 0 BIT05: Battery 2 Auto‑Wake‑up Switch 0: Disable, 1: Enable; default: Disable. BIT06: Scheduled Energy‑Saving Function Switch – 0: OFF, 1: ON; default: 0 Currently only used for ODM models. BIT07–15: Reserved Note: Operation instructions for writing BITxx: The host computer shall first read the current value of this register, then modify the value of the corresponding BIT as needed based on the current value, and fi- nally write the updated value back. |
| --- | --- | --- | --- | --- |
| 43376 | Battery Auto‑Wake‑up Duration Setting | U16 | 1S | Range: 20–300 s, default: 60 s S6 single‑phase high‑voltage 11.4 kW US models: Range: 20–300 s, default: 180 s Other S6 models: Range: 20–3600 s, default: 180 s |
| 43377 | Upgrade Type Selection | U16 |  | 00: Main DSP upgrade |

|  |  |  |  | 01: Secondary DSP upgrade (for 100 kW energy storage inverter) 05: AFCI board upgrade Note: Before performing an up- grade, each time an upgrade is in- itiated, the corresponding enable command must be sent (e.g., send 0 for main DSP, send 5 for AFCI board). |
| --- | --- | --- | --- | --- |
| 43378 | Single‑Function Opera- tion | U16 |  | 0x0000: Invalid 0x0001: CT detection function – after setting, read register 33290 to obtain the detection result. 0x0002: G100‑2022 fault manual clear. 0x0003: G100‑2022 fault restricted clear – specific clearing method is related to BIT01 of register 43290; refer to the G100 standard for de- tails. 0x0007: Load overload fault clear. 0x000A: Battery 2 manual wake‑up, only for models support- ing dual battery channels. 0x000E: AC Coupling Lock reset. 0x0012: Total grid‑side CT detec- tion and self‑adaptation start. 0x0013: EMS firmware upgrade confirmation x. 0x0014: EMS firmware upgrade confirmation x+1 (two writes con- firm the upgrade request). 0x0016~0xFFFF: Undefined. Description: - This register is used for sin- gle‑function operation settings. - Settings are not retained after power loss. |
| 43382 | Manual Master/Slave Setting | U16 |  | 0: Slave; 1: Master; Other values invalid. |
| 43384 | Inverter Connection Phase Setting | U16 |  | Range: 0–9; default 1. 0: Not set. 1: Single‑phase system. 2: Phase A of three‑phase system. |

|  |  |  |  | 3: Phase B of three‑phase system. 4: Phase C of three‑phase system. 5: Split‑phase system. 6: AB phase (split‑phase forming three‑phase). 7: BC phase (split‑phase forming three‑phase). 8: CA phase (split‑phase forming three‑phase). 9: ABC phase (three‑phase grid). Other values invalid. |
| --- | --- | --- | --- | --- |
| 43391 | Standalone/Parallel Set- ting | U16 |  | 0 – Standalone, 1 – Parallel; default 0. |
| 43481 | Over‑Discharge Hyste- resis SOC | U16 | 1% | Range: 1–20%, default 1%. Description: When battery SOC reaches the over‑discharge SOC, battery discharge is prohibited. Battery discharge becomes availa- ble again after SOC exceeds (over‑discharge SOC + over‑discharge hysteresis SOC). (Note: Over‑discharge SOC register address is 43011.) |
| 43482 | Battery Healing SOC | U16 | 1% | Range: 80–100%; default: 100%. |
| 43483 | Energy Storage Func- tion Control Word | U16 |  | BIT00: Smart Load enable – 0: disabled, 1: enabled, default 0. BIT01: AC Coupling enable – 0: disabled, 1: enabled, default 0. Note: Cannot be enabled simulta- neously with "With Generator" (BIT01 of register 43365); other- wise invalid – one must be turned off before the other is turned on. BIT02: Smart Load on‑grid always on (smart load port forced output when grid‑tied) – 0: disabled, 1: enabled, default 0. BIT03: Allow export switch under self‑consumption mode – 0: enabled, 1: disabled, default 0. BIT04: Backup2Load manual/auto switch – 0: manual, 1: auto, default 0. BIT05: Backup2Load manual on – |

|  |  |  |  | 0: invalid, 1: valid, default 0. BIT06: Smart Load off‑grid always off (smart load port stops output when off‑grid) – 0: disabled, 1: enabled, default 0. BIT07: Grid Peak‑shaving power enable – 0: disabled, 1: enabled, default 0. When disabled, battery charg- ing power is not limited based on public grid‑side power conditions. When enabled, if public grid‑side power draw exceeds the value set in register 43488, battery charging power is limited. BIT08–14: Reserved. BIT15: Not used; default 0. |
| --- | --- | --- | --- | --- |
| 43484 | AC Coupling Stop SOC | U16 | 1% | Range: 60–90%; default: 60%. |
| 43485 | AC Coupling Stop Vol- tage | U16 | 0.1V | Range: 50 V ~ equalization charge voltage setting; Default: 50 V; Note: Only applicable to battery types without communication ca- pability. |
| 43486 | AC Coupling Maxi- mum Load‑Shedding Frequency | U16 | 0.01Hz | Range: (National standard corres- ponding primary over‑frequency threshold + 0.1 Hz) ~ 54 Hz (50 Hz grid) / 65 Hz (60 Hz grid), Default: (National standard corres- ponding primary over‑frequency threshold + 0.1 Hz). |
| 43487 | Peak SOC | U16 | 1% | Range：0 ~ 100% |
| 43488 | Maximum Allowable Total Grid‑side Power Import | U16 | 100W | Indicates the active power value for single‑phase (or total per‑phase for three‑phase machines). Range: Standalone: 0 ~ unit rated input power Parallel: 0 ~ (unit rated input power × number of parallel units) Setting method V2 range: Standalone: 0 ~ unit rated in- put power × 4, default: unit rated input power Parallel: 0 ~ (unit rated input |

|  |  |  |  | power × 4 × number of parallel units), default: unit rated input power × number of parallel units Upper limit uniformly set to 3 MW. |
| --- | --- | --- | --- | --- |
| 43493 | TOU Scheduled Charg- ing Start Hour Setting 6 | U16 | hour | Description: - Only used for parameter settings in Optimization Revenue V1 ver- sion. - Takes effect when BIT01 of register 43110 is enabled. |
| 43494 | TOU Scheduled Charg- ing Start Minute Setting 6 | U16 | min |  |
| 43495 | TOU Scheduled Charg- ing End Hour Setting 6 | U16 | hour |  |
| 43496 | TOU Scheduled Charg- ing End Minute Setting 6 | U16 | min |  |
| 43497 | TOU Scheduled Dis- charging Start Hour Setting 6 | U16 | hour |  |
| 43498 | TOU Scheduled Dis- charging Start Minute Setting 6 | U16 | min |  |
| 43499 | TOU Scheduled Dis- charging End Hour Set- ting 6 | U16 | hour |  |
| 43500 | TOU Scheduled Dis- charging End Minute Setting 6 | U16 | min |  |
| 43630 | LG High Voltage Bat- tery Parallel Switch | U16 |  | 0: Off, 1: On. |
| 43631 | LG High Voltage Bat- tery Dead‑Zone Lower Limit | U16 | 0.1V | Range: 350–450V; default: 410 V. |
| 43632 | LG High Voltage Bat- tery Dead‑Zone Upper Limit | U16 | 0.1V | Range: 350~450V; default: 420V； |
| 43633 | LG High Voltage Bat- tery Charging Slope | U16 | 1 W/V | Range: 20–2000; 10H battery default: 250, 16H bat- tery default: 350. |
| 43634 | LG High Voltage Bat- tery Maximum Charg- | U16 | 0.1V | Range: 350–450 V; default: 450 V. |

|  | ing Voltage |  |  |  |
| --- | --- | --- | --- | --- |
| 43635 | LG High Voltage Bat- tery Discharging Slope | U16 | 1W/V | Range: 20–2000; 10H battery default: 250, 16H bat- tery default: 350. |
| 43636 | LG High Voltage Bat- tery Maximum Dis- charging Voltage | U16 | 0.1V | Range: 350–450 V; default: 350 V. |
| 43637 | LG High Voltage Bat- tery Charging Limit Power | U16 | 1W | 10H battery range: 0–5000 W; 16H battery range: 0–7000 W. |
| 43638 | LG High Voltage Bat- tery Discharging Limit Power | U16 | 1W | 10H battery range: 0–7000 W; 16H battery range: 0–11000 W. |
| 43639 | LG High Voltage Bat- tery Communication Fault Timeout | U16 | 0.5min | Range: 0.5–1440 min; default: 10 minutes. |
| 43640~ 43641 | LG High Voltage Bat- tery Sleep Hold Time | U32 | 1s | Range: 0–86400; default: 86400. |
| 43642 | LG High Voltage Bat- tery Black‑Start Enable | U16 |  | Range: 0–1; default: 0. In battery parallel configuration, only sent to the master battery. |
| 43643 | LG High‑Voltage Bat- tery Black‑Start Initia- lization Time | U16 | 1s | Range: 5–200 s; default: 15 s. |
| 43650 | Backup Load Droop Control Minimum Vol- tage | U16 | 0.1V | Standard‑voltage models: phase voltage range 120–230 V, default 180 V. Low‑voltage models: phase voltage range 70–130 V, default 100 V; Line voltage range 120–230 V, de- fault 180 V. |
| 43672 | Smart Load Turn‑off SOC | U16 | 1% | Range: over‑discharge SOC (start SOC = 5%) to default 85%. Note: This setting takes effect only when BIT02 (smart load port forced grid‑tied output) of register 43483 is disabled. |
| 43673 | Smart Load Turn‑on SOC | U16 | 1% | Range: (over‑discharge SOC + 5%) to 100%, default 90%, and turn‑off SOC ≤ turn‑on SOC – 5%. Note: This setting takes effect only when BIT02 (smart load port forced grid‑tied output) of register 43483 is disabled. |

| 43674 | Smart Load Turn‑off Battery Voltage | U16 | 0.1V | Range: 45–57 V, default 52 V, and turn‑off battery voltage ≤ turn‑on battery voltage – 3 V. Note: (1) Takes effect only after "Follow Grid" is set to Enable. (2) This set- ting takes effect only when BIT02 (smart load port forced grid‑tied output) of register 43483 is dis- abled. |
| --- | --- | --- | --- | --- |
| 43675 | Smart Load Turn‑on Battery Voltage | U16 | 0.1V | Range: 50–60 V, default 55 V. Note: (1) Takes effect only after "Follow Grid" is set to Enable. (2) This set- ting takes effect only when BIT02 (smart load port forced grid‑tied output) of register 43483 is dis- abled. |
| 43676 | Over‑Discharge Full Recovery Voltage | U16 | 0.1V | Range: 2.0–7.0 V, default 3 V. Note: Used for lead‑acid batteries and 48 V/51.2 V non‑communication li- thium batteries. |
| 43677 | Off‑Grid Battery Over‑Discharge SOC Function Switch | U16 |  | 1: Off, 2: On (register 43137 func- tion takes effect), other values invalid. Default: 1. |
| 43705 | EPS Function Control | U16 |  | 0xA5 – Disabled; Backup relay is controlled according to register 43111 “Backup Load Function En- able”. 0x5A – Enabled; when grid‑tied, the Backup relay is forced open; when off‑grid, it closes after a delay (time configurable). Default: 0xA5; other values invalid. |
| 43707 | TOU Grid‑Tied Opti- mization Revenue V2 Switch | U16 |  | When using this function, first read register 33289 to determine whether Optimization Revenue V2 is valid. If it is invalid, the Optimization Revenue V1 func- tion must be used. BIT00: Grid‑tied charging period 1 switch – 0: off, 1: on, default 0. BIT01: Grid‑tied charging period 2 switch – 0: off, 1: on, default 0. |

|  |  |  |  | BIT02: Grid‑tied charging period 3 switch – 0: off, 1: on, default 0. BIT03: Grid‑tied charging period 4 switch – 0: off, 1: on, default 0. BIT04: Grid‑tied charging period 5 switch – 0: off, 1: on, default 0. BIT05: Grid‑tied charging period 6 switch – 0: off, 1: on, default 0. BIT06: Grid‑tied discharging pe- riod 1 switch – 0: off, 1: on, default 0. BIT07: Grid‑tied discharging pe- riod 2 switch – 0: off, 1: on, default 0. BIT08: Grid‑tied discharging pe- riod 3 switch – 0: off, 1: on, default 0. BIT09: Grid‑tied discharging pe- riod 4 switch – 0: off, 1: on, default 0. BIT10: Grid‑tied discharging pe- riod 5 switch – 0: off, 1: on, default 0. BIT11: Grid‑tied discharging period 6 switch – 0: off, 1: on, default 0. BIT12–15: Reserved, default 0. Operation instructions for writing BITxx: The host computer shall first read the current value of this register, then modify the value of the corresponding BIT as needed based on the current value, and fi- nally write the updated value back. |
| --- | --- | --- | --- | --- |
| 43708 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 1 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. |
| 43709 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 1 Bat- tery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum charging current, Default: unit rated battery maxi- mum charging current. |
| 43710 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 1 | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. |

|  | Cut‑off Voltage |  |  | Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| --- | --- | --- | --- | --- |
| 43711 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 1 Start Hour | U16 | 1Hour |  |
| 43712 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 1 Start Minute | U16 | 1Min |  |
| 43713 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 1 End Hour | U16 | 1Hour |  |
| 43714 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 1 End Minute | U16 | 1Min |  |
| 43715 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 2 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43716 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 2 Bat- tery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum charging current, Default: unit rated battery maxi- mum charging current. |
| 43717 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 2 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. |

|  |  |  |  | 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| --- | --- | --- | --- | --- |
| 43718 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 2 Start Hour | U16 | 1Hour |  |
| 43719 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 2 Start Minute | U16 | 1Min |  |
| 43720 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 2 End Hour | U16 | 1Hour |  |
| 43721 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 2 End Minute | U16 | 1Min |  |
| 43722 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 3 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43723 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 3 Bat- tery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum charging current, Default: unit rated battery maxi- mum charging current. |
| 43724 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 3 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. |

|  |  |  |  | 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| --- | --- | --- | --- | --- |
| 43725 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 3 Start Hour | U16 | 1Hour |  |
| 43726 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 3 Start Minute | U16 | 1Min |  |
| 43727 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 3 End Hour | U16 | 1Hour |  |
| 43728 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 3 End Minute | U16 | 1Min |  |
| 43729 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 4 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43730 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 4 Bat- tery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum charging current, Default: unit rated battery maxi- mum charging current. |
| 43731 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 4 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |

| 43732 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 4 Start Hour | U16 | 1Hour |  |
| --- | --- | --- | --- | --- |
| 43733 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 4 Start Minute | U16 | 1Min |  |
| 43734 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 4 End Hour | U16 | 1Hour |  |
| 43735 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 4 End Minute | U16 | 1Min |  |
| 43736 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 5 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43737 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 5 Bat- tery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum charging current, Default: unit rated battery maxi- mum charging current. |
| 43738 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 5 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| 43739 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 5 Start Hour | U16 | 1Hour |  |

| 43740 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 5 Start Minute | U16 | 1Min |  |
| --- | --- | --- | --- | --- |
| 43741 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 5 End Hour | U16 | 1Hour |  |
| 43742 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 5 End Minute | U16 | 1Min |  |
| 43743 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 6 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43744 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 6 Bat- tery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum charging current, Default: unit rated battery maxi- mum charging current. |
| 43745 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 6 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| 43746 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 6 Start Hour | U16 | 1Hour |  |
| 43747 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 6 Start Minute | U16 | 1Min |  |

| 43748 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 6 End Hour | U16 | 1Hour |  |
| --- | --- | --- | --- | --- |
| 43749 | TOU Optimization Revenue V2: Grid‑Tied Charging Period 6 End Minute | U16 | 1Min |  |
| 43750 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 1 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43751 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 1 Battery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum discharging current, Default: unit rated battery maxi- mum discharging current. |
| 43752 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 1 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| 43753 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 1 Start Hour | U16 | 1Hour |  |
| 43754 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 1 Start Minute | U16 | 1Min |  |
| 43755 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 1 End Hour | U16 | 1Hour |  |

| 43756 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 1 End Minute | U16 | 1Min |  |
| --- | --- | --- | --- | --- |
| 43757 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 2 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43758 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 2 Battery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum discharging current, Default: unit rated battery maxi- mum discharging current. |
| 43759 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 2 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| 43760 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 2 Start Hour | U16 | 1Hour |  |
| 43761 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 2 Start Minute | U16 | 1Min |  |
| 43762 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 2 End Hour | U16 | 1Hour |  |
| 43763 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 2 End Minute | U16 | 1Min |  |

| 43764 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 3 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| --- | --- | --- | --- | --- |
| 43765 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 3 Battery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum discharging current, Default: unit rated battery maxi- mum discharging current. |
| 43766 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 3 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| 43767 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 3 Start Hour | U16 | 1Hour |  |
| 43768 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 3 Start Minute | U16 | 1Min |  |
| 43769 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 3 End Hour | U16 | 1Hour |  |
| 43770 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 3 End Minute | U16 | 1Min |  |
| 43771 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 4 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with |

|  |  |  |  | SOC capability. |
| --- | --- | --- | --- | --- |
| 43772 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 4 Battery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum discharging current, Default: unit rated battery maxi- mum discharging current. |
| 43773 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 4 Cut‑off Voltage | U16 | 0.1V | 10<-->1V ； For batteries without SOC capability, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| 43774 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 4 Start Hour | U16 | 1Hour |  |
| 43775 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 4 Start Minute | U16 | 1Min |  |
| 43776 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 4 End Hour | U16 | 1Hour |  |
| 43777 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 4 End Minute | U16 | 1Min |  |
| 43778 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 5 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43779 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 5 | U16 | 0.1A | Range: 0 – unit rated battery max- imum discharging current, Default: unit rated battery maxi- |

|  | Battery Current |  |  | mum discharging current. |
| --- | --- | --- | --- | --- |
| 43780 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 5 Cut‑off Voltage | U16 | 0.1V | For batteries without SOC capabil- ity, including lead‑acid batteries and 48 V/51.2 V batteries. Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| 43781 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 5 Start Hour | U16 | 1Hour |  |
| 43782 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 5 Start Minute | U16 | 1Min |  |
| 43783 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 5 End Hour | U16 | 1Hour |  |
| 43784 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 5 End Minute | U16 | 1Min |  |
| 43785 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 6 Cut‑off SOC | U16 | 1% | Range: (Over‑discharge SOC + 1%) to 100%, Default: 50%. Note: For lithium batteries with SOC capability. |
| 43786 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 6 Battery Current | U16 | 0.1A | Range: 0 – unit rated battery max- imum discharging current, Default: unit rated battery maxi- mum discharging current. |
| 43787 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 6 | U16 | 0.1V | 10<-->1V ； For batteries without SOC capability, including lead‑acid batteries and 48 V/51.2 V batteries. |

|  | Cut‑off Voltage |  |  | Lead‑acid battery range: (Over‑discharge voltage + 0.5 V) ~ (Float charge voltage – 0.5 V), de- fault: 49.5 V. 48 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 49.0 V. 51.2 V battery range: (Over‑discharge voltage + 0.5 V) ~ (Equalization charge voltage – 2.5 V), default: 52.0 V. |
| --- | --- | --- | --- | --- |
| 43788 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 6 Start Hour | U16 | 1Hour |  |
| 43789 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 6 Start Minute | U16 | 1Min |  |
| 43790 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 6 End Hour | U16 | 1Hour |  |
| 43791 | TOU Optimization Revenue V2: Grid‑Tied Discharging Period 6 End Minute | U16 | 1Min |  |
| 43792 | Generator Minimum Input Power | U16 | 10W | Range: 0 – unit rated value × num- ber of parallel units Default: 1 kW. |
| 43802 | Dual‑Battery Connec- tion Mode | U16 |  | 1: Battery Independent, 2Batt2DC 2: Battery Shared, 1Batt2DC 3: Single battery connected to one battery port – 1Batt1DC Other values: Invalid Default: 1 Note: Applicable to models sup- porting dual‑battery configuration. |
| 43803 | Battery 2 Type Setting | U16 |  | For details, see Appendix 6: Battery Numbering. Battery 2 settings are only applicable to energy storage models that support dual‑battery configurations. |

| 43804 | Battery 2 Maximum Charging Current Set- ting | U16 | 0.1A |  |
| --- | --- | --- | --- | --- |
| 43805 | Battery 2 Maximum Discharging Current Setting | U16 | 0.1A |  |
| 43806 | Battery 2 Un- der‑Voltage Protection Setting | U16 | 0.1V |  |
| 43808 | Battery 2 Equalization Charge Voltage Setting | U16 | 0.1V |  |
| 43809 | Battery 2 Over‑Voltage Protection Setting | U16 | 0.1V |  |
| 43810 | Battery 2 Over‑Discharge SOC | U16 | 1% |  |
| 43811 | Battery 2 Over‑Discharge Hyste- resis SOC | U16 | 1% |  |
| 43812 | Battery 2 Forced Charge SOC | U16 | 1% |  |
| 43813 | Battery 2 Au- to‑Wake‑up Duration Setting | U16 | 1s | Range: 20–3600 s, default: 180 s. |
| 43814 | Battery 2 Type Setting Follows Battery 1. | U16 |  | 0xAA55: Follow – the read para- meters for Battery 2 are consistent with Battery 1, and writing to the Battery 2 type setting register is invalid. Other values: Do not follow – writ- ing to Battery 2 related setting reg- isters is valid. Default: 0 (i.e., do not follow). Note: Applicable to models sup- porting dual‑battery configurations. |
| 43858 | Battery 2 Wake‑up Vol- tage | U16 | 0.1V | Low‑voltage energy storage unit: 40–60 V, default 40 V. Off‑grid energy storage unit: 40–60 V, default 40 V. Single‑phase high‑voltage energy storage unit: 120–500 V, default 120 V. Three‑phase high‑voltage energy storage unit: 120–600 V, default 120 V. |

|  |  |  |  | Note: Takes effect only when BIT12 (battery wake‑up trigger action) of register 43110 is enabled. |
| --- | --- | --- | --- | --- |
| 43859 | Battery 2 Wake‑up Time | U16 | 1s | Range: 20–3600 s, default: 20 s. |
| 43860 | PCS Limiting Mode Setting | U16 |  | PCS Anti‑Reverse‑Flow Limiting Mode Settings: 0: No limit mode (no restriction on energy exchange between battery and grid). 1: Output limit mode (only battery discharge to the grid is allowed; battery charging from the grid is prohibited). 2: Input limit mode (only battery charging from the grid is allowed; battery discharge to the grid is pro- hibited). 3: No‑exchange mode (battery charging from the grid is prohi- bited, and battery discharge to the grid is also prohibited). Settings are retained after power loss. Currently only supported for S6 single‑phase high‑voltage ener- gy storage systems. |
| 43861 | Grid‑Side Load Sin- gle‑Phase Protection Current Limit | U16 | 1A | When the current of the load con- nected to the distribution panel ex- ceeds the protection limit of the distribution panel, the inverter switches to off‑grid operation. At this point, the overload protection device activates to ensure the dis- tribution panel current does not exceed the user‑defined limit. This function becomes effective after the PCS limiting mode is enabled (i.e., when register 43860 is not 0) and operates under the condition that protection in register 43871 is enabled. Settings are retained after power loss. Currently only supported for |

|  |  |  |  | S6 single‑phase high‑voltage ener- gy storage systems. |
| --- | --- | --- | --- | --- |
| 43862 | PCS Input Limit Bat- tery Current Limit | U16 | 0.1A | When the PCS limiting mode is configured as input limit mode, this is the allowable current limit for battery charging from the grid. Set- ting range: 0 A – maximum battery current of the current model. De- fault value: maximum battery cur- rent of the current model. Settings are retained after power loss. Currently only supported for S6 single‑phase high‑voltage ener- gy storage systems. |
| 43863 | PCS Output Limit Bat- tery Current Limit | U16 | 0.1A | When the PCS limiting mode is configured as output limit mode, this is the allowable current limit for battery discharging to the grid. Setting range: 0 A – maximum bat- tery current of the current model. Default value: maximum battery current of the current model. Settings are retained after power loss. Currently only supported for S6 single‑phase high‑voltage ener- gy storage systems. |
| 43864 | PV Inverter AC Output Side CT Ratio | U16 | 1 | Range: 1–2000, default: 1000. Settings are retained after power loss. Currently only supported for S6 AC Coupled models. |
| 43871 | Grid‑Side Load Sin- gle‑Phase Overcurrent Protection Switch | U16 |  | 0 – Off, 1 – On, default: 1. Other values: Invalid. |
| 43885 | Heat Pump Function Switch | U16 |  | BIT00: Heat pump function master switch – 0: Off, 1: On, default 0. BIT01: Heat pump manual mode – 0: Normal, 1: Enhanced, default 0. BIT02: Heat pump scheduled en- hancement switch – 0: Off, 1: On, default 0. BIT03: Heat pump intelligent con- trol mode switch – 0: Off, 1: On, |

|  |  |  |  | default 0. BIT04–15: Reserved. |
| --- | --- | --- | --- | --- |
| 43886 | Heat Pump Minimum Control Time Interval | U16 | 1min | Range: 5–60, default: 10. |
| 43971 | Heat Pump Intelligent Control Mode Start SOC | U16 | 1% | Range: (Over‑discharge SOC + 5%) to 100%, default: 90%. Note: Over‑discharge SOC register address is 43011. |
| 43972 | Heat Pump Intelligent Control Mode Stop SOC | U16 | 1% | Range: Over‑discharge SOC to (Start SOC – 5%), default: 70%. |
| 43973 | Heat Pump Intelligent Control Mode Start Voltage | U16 | 0.1V | Start voltage ≥ (Stop voltage + 2 V) Range: 42.0 – 60.0 V (max 59.5 V) Default: Lead‑acid battery: 55 V, 48 V non‑communication lithium battery: 51.5 V, 51.2 V non‑communication lithium battery: 55 V. |
| 43974 | Heat Pump Intelligent Control Mode Stop Voltage | U16 | 0.1V | Start voltage ≥ (Stop voltage + 2 V) Range: 40.0 – 60.0 V (max 57.5 V) Default: Lead‑acid battery: 50 V, 48 V non‑communication lithium battery: 49 V, 51.2 V non‑communication lithium battery: 52 V. |
| 43975~ 43976 | Maximum Total Feed‑in Active Power under Phase Unbalance Mode | S32 | 1W | Indicates the sum of active power from all phases. Standalone range: 0–1,000,000 W, default: 1.1 times the unit rated power. Parallel range: 0–1,000,000 W, de- fault: 1.1 times the unit rated power × number of parallel units. Note: Only applicable to S6‑generation three‑phase high‑voltage 10 kW series energy storage machines and S6‑generation single‑phase high‑voltage US‑version machines. |
| 43977 | Paid leasing function | U16 |  | 0x0000: Off 0x0001: On Default: 0x0000 (Off), other values |

|  |  |  |  | invalid. |
| --- | --- | --- | --- | --- |
| 43978 | Paid Rental Equipment Lock Function Switch – Lock | U16 |  | 0x0000: Off 0x0001: On Default: 0x0000 (Off), other values invalid. Only effective when the paid rental function is enabled (register 43977 = 0xAA55, 0x0001). |
| 43984 | Heat Pump Intelligent Control Mode Enable Power | S16 | 0.1kW | Range: 0.1–1000 kW, default: 2 kW. Enable power > Disable power. |
| 43985 | Heat Pump Intelligent Control Mode Disable Power | S16 | 0.1kW | Range: –5 to 10 kW, default: –0.5 kW. Enable power > Disable power. |
| 43989 | AC coupling Max Ex- port Control | U16 |  | 0：None 1：Based on Export Power&SOC 2：Second RS485(Only for Solis INV) Other values invalid; default: 0. |
| 43998 | Dynamic Reactive Power Compensation Switch | U16 |  | 0: Off, 1: On, default: Off. Meaning: When Dynamic Reactive Power Compensation (SVG) is enabled, the inverter automatically compensates the reactive power at the total grid port. |
| 44099 | AC Coupling Con- nected to AC Side | U16 |  | 0x01 – Disabled, 0x02 – Enabled, Other values invalid, default: 0x01. |
| 44100 | Remote Dispatch Mode Switch | U16 |  | 0: Off, 1: On, default 0, other val- ues invalid. Description: This function takes effect when register 34502 = 0xAA55; specific function mapping corresponds to 34503. Registers 44100–44199 are used to configure the remote dispatch mode. All setting values related to the re- mote dispatch mode are not re- tained after power loss. Recommendation: The host com- puter should write to the inverter in three parts: 44100–44104 represent the overall |

|  |  |  |  | remote dispatch settings. 44105–44115 represent remote dispatch real‑time control. 44116–44199 represent remote dispatch time‑scheduled control (send no more than 50 registers at a time: Periods 1–3 (42 registers) in one write, periods 4–6 (42 registers) in one write). |
| --- | --- | --- | --- | --- |
| 44101 | Remote Dispatch Mode – Failsafe Interval | U16 | 1min | Range: 1–1440, default: 5; out‑of‑range settings are invalid. |
| 44102 | Remote Dispatch Mode – System Limiting Switch | U16 |  | BIT00: System power‑draw active power upper‑limit switch – 0: Dis- abled, 1: Enabled (system pow- er‑draw active power upper‑limit setting takes effect), default 0. BIT01: System feed‑in active pow- er upper‑limit switch – 0: Disabled, 1: Enabled (system feed‑in active power upper‑limit setting takes ef- fect), default 0. BIT02–15: Reserved. |
| 44103 | Remote Dispatch Mode – System Power‑Draw Active Power Upper Limit | U16 | 100W | Standalone range: 0 ~ 4 × unit maximum rated value, Upper limit uniformly set to 3 MW (related to register 34806 bits 06‑07). Parallel range: 0 ~ 4 × unit maxi- mum rated value × number of pa- rallel units, Upper limit uniformly set to 3 MW (related to register 34806 bits 06‑07). Default: Inverter maximum rated output power × number of parallel units. Out‑of‑range recovery to default: (Example: When the upper‑limit switch is enabled, writing 0xFFFF restores the default value.) |
| 44104 | Remote Dispatch Mode – System Feed‑in Ac- tive Power Upper Limit | U16 | 100W | Standalone range: 0 ~ 4 × unit maximum rated value, Upper limit uniformly set to 3 |

|  |  |  |  | MW (related to register 34806 bits 06‑07). Parallel range: 0 ~ 4 × unit maxi- mum rated value × number of pa- rallel units, Upper limit uniformly set to 3 MW (related to register 34806 bits 06‑07). Default: Inverter maximum rated output power × number of parallel units. Out‑of‑range recovery to default: (Example: When the upper‑limit switch is enabled, writing 0xFFFF restores the default value.) |
| --- | --- | --- | --- | --- |
| 44105 | Remote Dispatch Mode – Real‑Time Control – Control Mode | U16 |  | - – Battery Standby control (no charging/discharging) - – Battery charge/discharge con- trol - – Point of Common Coupling (PCC) Import/Export control - – AC Grid port Import/Export control - – Self‑consumption control - – Grid‑feed priority control Default: 1, other values invalid. |
| 44106~ 44107 | Remote Dispatch Mode – Real‑Time Control – Power Setting | S32 | 10W | The function is determined by the control mode in register 44105. Default: 0; out‑of‑range settings are invalid. - When the control mode is 1, this power value has no effect. - When the control mode is 2: Negative values indicate bat- tery discharge power, positive val- ues indicate battery charging power. Range: –(maximum charge/discharge power × number of parallel units) ~ +(maximum charge/discharge power × number of parallel units). - When the control mode is 3: Negative values indicate Im- port power, positive values indicate |

|  |  |  |  | Export power. Range: –(inverter maximum output power × number of parallel units) ~ +(inverter maximum output power × number of parallel units). (4) When the control mode is 4: Negative values indicate Im- port power, positive values indicate Export power. Range: –(inverter maximum output power × number of parallel units) ~ +(inverter maximum output power × number of parallel units). |
| --- | --- | --- | --- | --- |
| 44108 | Remote Dispatch Mode – Real‑Time Control – Function Switch | U16 |  | BIT00–BIT01: PV Shutdown con- trol – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT02–BIT03: DO control – 0: invalid, 1: open, 2: closed, 3: invalid, default 0. BIT04–BIT05: Allow grid‑to‑battery charging – 0: invalid, 1: allowed, 2: not allowed, 3: invalid, default 0. BIT06–BIT07: Off‑grid battery standby – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT08–BIT09: Battery reserve (used with register 44111) – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT10–BIT11: Battery discharge disable – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT12–BIT13: Demand control – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT14–BIT15: PV power‑limit percentage switch –0: invalid, 1: disabled, 2: enabled, 3: invalid, de- fault 0. Note: After writing “invalid” data, reading this register returns the last valid data written. Example: first write 1, then write 0; the read data |

|  |  |  |  | will be 1. |
| --- | --- | --- | --- | --- |
| 44109 | Remote Dispatch Mode – Real‑Time Control – SOC Lower Limit | U16 | 1% | Range: 0 to Real‑Time Control SOC Upper Limit, default 0. If out of range or greater than/equal to the Real‑Time Control SOC Up- per Limit, the setting is invalid. |
| 44110 | Remote Dispatch Mode – Real‑Time Control – SOC Upper Limit | U16 | 1% | Range: Real‑Time Control SOC Lower Limit to 100%, default 100%. If out of range or less than/equal to the Real‑Time Control SOC Lower Limit, the setting is invalid. |
| 44111 | Remote Dispatch Mode – Real‑Time Control – Battery Reserve SOC | U16 | 1% | Range: Over‑discharge SOC to Real‑Time Control Upper Limit SOC, default 40%. Description: - Over‑discharge SOC is set in register 43011; Real‑Time Control Upper Limit SOC is set in register 44110. - Only effective when battery reserve is enabled in register 44108. |
| 44112 | Remote Dispatch Mode – Real‑Time Control – PV Power‑Limit Per- centage | U16 | 0.01% | 100 <--> 1% Description: (1) Takes effect when the PV power‑limit percentage switch is enabled. |
| 44113 | Remote Dispatch Mode – Real‑Time Control – Reserved 3 | U16 |  |  |
| 44114 | Remote Dispatch Mode – Real‑Time Control – Reserved 4 | U16 |  |  |
| 44115 | Remote Dispatch Mode – Real‑Time Control – Reserved 5 | U16 |  |  |
| 44116 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Switch | U16 |  | 0: Disabled 1: Enabled Default 0, other values invalid. |
| 44117 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Start Time Setting | U16 |  | High byte: Hour, range 0–23, de- fault 0, other values invalid. Low byte: Minute, range 0–59, de- fault 0, other values invalid. Enabled time periods must not overlap. If periods overlap, only the |

|  |  |  |  | period with the lower segment number will be executed. Example: If period 1 is set to 01:00–05:00 and period 2 is set to 03:00–06:00, because of time over- lap, only period 1 control will be executed. |
| --- | --- | --- | --- | --- |
| 44118 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – End Time Setting | U16 |  | High byte: Hour, range 0–23, de- fault 0, other values invalid. Low byte: Minute, range 0–59, de- fault 0, other values invalid. |
| 44119 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Con- trol Mode | U16 |  | - – Battery Standby control (no charging/discharging) - – Battery charge/discharge con- trol - – Point of Common Coupling (PCC) Import/Export control - – AC Grid port Import/Export control - – Self‑consumption control - – Grid‑feed priority control Default: 1, other values invalid. |
| 44120~ 44121 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Power Setting | S32 | 10W | The function is determined by the control mode in register 44105. Default: 0; out‑of‑range settings are invalid. - When the control mode is 1, this power value has no prac- tical effect. - When the control mode is 2, negative values indicate bat- tery discharge power, positive val- ues indicate battery charging power. Range: –(maximum charge/discharge power × number of parallel units) ~ +(maximum charge/discharge power × number of parallel units). - When the control mode is 3, negative values indicate Im- port power, positive values indicate Export power. Range: –(inverter maximum output power × number of parallel |

|  |  |  |  | units) ~ +(inverter maximum output power × number of parallel units). (4) When the control mode is 4, negative values indicate Im- port power, positive values indicate Export power. Range: –(inverter maximum output power × number of parallel units) ~ +(inverter maximum output power × number of parallel units). |
| --- | --- | --- | --- | --- |
| 44122 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Func- tion Switch | U16 |  | BIT00–BIT01: PV Shutdown con- trol – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT02–BIT03: DO control – 0: invalid, 1: open, 2: closed, 3: invalid, default 0. BIT04–BIT05: Allow grid‑to‑battery charging –0: invalid, 1: allowed, 2: not allowed, 3: invalid, default 0. BIT06–BIT07: Off‑grid battery standby – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT08–BIT09: Battery reserve (used with register 44111) – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT10–BIT11: Battery discharge disable – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT12–BIT13: Demand control – 0: invalid, 1: disabled, 2: enabled, 3: invalid, default 0. BIT14–BIT15: PV power‑limit percentage switch – 0: invalid, 1: disabled, 2: enabled, 3: invalid, de- fault 0. Note: After writing “invalid” data, reading this register returns the last valid data written. Example: first write 1, then write 0; the read data will be 1. |
| 44123 | Remote Dispatch Mode – Time‑Scheduled Con- | U16 |  | Range: 0 to Period 1 SOC Upper Limit, default 0. |

|  | trol – Period 1 – SOC Lower Limit |  |  | If out of range or greater than/equal to Period 1 SOC Upper Limit, the setting is invalid. |
| --- | --- | --- | --- | --- |
| 44124 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – SOC Upper Limit | U16 |  | Range: Period 1 SOC Lower Limit to 100%, default 100%. If out of range or less than/equal to Period 1 SOC Lower Limit, the setting is invalid. |
| 44125 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Battery Reserve SOC | U16 |  | Range: Over‑discharge SOC to Time‑Scheduled Control Period 1 Upper Limit SOC, default 40%. Description: - Over‑discharge SOC is set in register 43011; Time‑Scheduled Control Pe- riod 1 Upper Limit SOC is set in register 44124. - Only effective when battery reserve is enabled in register 44108. |
| 44126 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – PV Power‑Limit Percentage | U16 |  | 100 <--> 1% Description: (1) Takes effect when the PV power‑limit percentage switch (bits 14‑15 of register 44122) is enabled. |
| 44127 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Re- served 3 | U16 |  |  |
| 44128 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Re- served 4 | U16 |  |  |
| 44129 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 1 – Re- served 5 | U16 |  |  |
| 44130 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Switch | U16 |  | The content format of Segment 2 is the same as Segment 1. |
| 44131 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Start Time Setting | U16 |  |  |
| 44132 | Remote Dispatch Mode | U16 |  |  |

|  | – Time‑Scheduled Con- trol – Period 2 – End Time Setting |  |  |  |
| --- | --- | --- | --- | --- |
| 44133 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Con- trol Mode | U16 |  |  |
| 44134~ 44135 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Power Setting | S32 |  |  |
| 44136 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Func- tion Switch | U16 |  |  |
| 44137 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – SOC Lower Limit | U16 |  |  |
| 44138 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – SOC Upper Limit | U16 |  |  |
| 44139 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Re- served 1 | U16 |  |  |
| 44140 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Re- served 2 | U16 |  |  |
| 44141 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Re- served 3 | U16 |  |  |
| 44142 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Re- served 4 | U16 |  |  |
| 44143 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 2 – Re- served 5 | U16 |  |  |
| 44144 | Remote Dispatch Mode | U16 |  | The content format of Segment 3 is |

|  | – Time‑Scheduled Con- trol – Period 3 – Switch |  |  | the same as Segment 1. |
| --- | --- | --- | --- | --- |
| 44145 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Start Time Setting | U16 |  |  |
| 44146 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – End Time Setting | U16 |  |  |
| 44147 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Con- trol Mode | U16 |  |  |
| 44148~ 44149 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Power Setting | S32 |  |  |
| 44150 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Func- tion Switch | U16 |  |  |
| 44151 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – SOC Lower Limit | U16 |  |  |
| 44152 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – SOC Upper Limit | U16 |  |  |
| 44153 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Re- served 1 | U16 |  |  |
| 44154 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Re- served 2 | U16 |  |  |
| 44155 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Re- served 3 | U16 |  |  |
| 44156 | Remote Dispatch Mode – Time‑Scheduled Con- | U16 |  |  |

|  | trol – Period 3 – Re- served 4 |  |  |  |
| --- | --- | --- | --- | --- |
| 44157 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 3 – Re- served 5 | U16 |  |  |
| 44158 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Switch | U16 |  | The content format of Segment 4 is the same as Segment 1. |
| 44159 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Start Time Setting | U16 |  |  |
| 44160 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – End Time Setting | U16 |  |  |
| 44161 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Con- trol Mode | U16 |  |  |
| 44162~ 44163 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Power Setting | S32 |  |  |
| 44164 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Func- tion Switch | U16 |  |  |
| 44165 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – SOC Lower Limit | U16 |  |  |
| 44166 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – SOC Upper Limit | U16 |  |  |
| 44167 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Re- served 1 | U16 |  |  |
| 44168 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Re- | U16 |  |  |

|  | served 2 |  |  |  |
| --- | --- | --- | --- | --- |
| 44169 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Re- served 3 | U16 |  |  |
| 44170 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Re- served 4 | U16 |  |  |
| 44171 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 4 – Re- served 5 | U16 |  |  |
| 44172 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Switch | U16 |  | The content format of Segment 5 is the same as Segment 1. |
| 44173 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Start Time Setting | U16 |  |  |
| 44174 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – End Time Setting | U16 |  |  |
| 44175 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Con- trol Mode | U16 |  |  |
| 44176~ 44177 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Power Setting | S32 |  |  |
| 44178 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Func- tion Switch | U16 |  |  |
| 44179 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – SOC Lower Limit | U16 |  |  |
| 44180 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – SOC Upper Limit | U16 |  |  |

| 44181 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Re- served 1 | U16 |  |  |
| --- | --- | --- | --- | --- |
| 44182 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Re- served 2 | U16 |  |  |
| 44183 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Re- served 3 | U16 |  |  |
| 44184 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Re- served 4 | U16 |  |  |
| 44185 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 5 – Re- served 5 | U16 |  |  |
| 44186 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Switch | U16 |  | The content format of Segment 6 is the same as Segment 1. |
| 44187 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Start Time Setting | U16 |  |  |
| 44188 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – End Time Setting | U16 |  |  |
| 44189 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Con- trol Mode | U16 |  |  |
| 44190~ 44191 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Power Setting | S32 |  |  |
| 44192 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Func- tion Switch | U16 |  |  |
| 44193 | Remote Dispatch Mode | U16 |  |  |

|  | – Time‑Scheduled Con- trol – Period 6 – SOC Lower Limit |  |  |  |
| --- | --- | --- | --- | --- |
| 44194 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – SOC Upper Limit | U16 |  |  |
| 44195 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Re- served 1 | U16 |  |  |
| 44196 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Re- served 2 | U16 |  |  |
| 44197 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Re- served 3 | U16 |  |  |
| 44198 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Re- served 4 | U16 |  |  |
| 44199 | Remote Dispatch Mode – Time‑Scheduled Con- trol – Period 6 – Re- served 5 | U16 |  |  |
| 44202 | ARM EMS Port Baud Rate Setting | U16 |  | Baud Rate List: 96 <->9600bps， 192<->19200bps， 384<->38400bps； 576<->57600bps； 1152<->115200bps； Other values invalid. Note: Currently only supported for 50 kW series energy storage units. |
| 44205 | Utility Bypass Function Switch Setting | U16 |  | 0：Disable，1：Enable； Default: Disable； |
| 44220~ 44221 | PV Storage System Grid‑tied Inverter Total Capacity | U32 | 0.1kW | Range：10~50000(Upper limit: 5 MW) |
| 44222 | PV Storage System Grid‑tied Inverter Quantity | U16 |  | Range：0~20，default: 0 |

| 44223 | PV Storage System An- ti‑Reverse‑Flow Con- trol Strategy | U16 |  | 1: High precision, 2: Fast, other values invalid, default 1. |
| --- | --- | --- | --- | --- |
| 44224 | PV Storage System An- ti‑Reverse‑Flow Con- trol Mode | U16 |  | 1: Three‑phase power sum mode, 2: Three‑phase minimum power mode, other values invalid, default 1. |
| 44225~ 44226 | PV Storage System To- tal Grid‑side Active Power Control Com- pensation | S32 | 1W | Range：-243750W ~ +243750W |
| 44227~ 44228 | PV Storage System Maximum Feed‑in Total Active Power Setting | U32 | 0.001 kW | Range：0~4875kW，Default: Unit rated AC output power × 1.1 |
| 44229~ 44230 | PV Storage System Maximum Feed‑in Hard Limit Power Setting | U32 | 0.001 kW | Range：0~4875kW，Default: Unit rated AC output power × 1.1 Applicable to Australian an- ti‑reverse‑flow requirements. |
| 44231~ 44232 | PV Storage System G100‑2022 Standard Total Grid‑side Current Output Limit Setting | U32 | 0.01A | Range ： 0~7386A ， Default: unit rated AC output current × 1.1. Applicable to UK anti‑reverse‑flow requirements. |
| 44233 | PV Storage System Meter 1 PT Voltage Ra- tio | U16 |  | Range：1~30000 |
| 44236 | PV Storage System Meter 2 PT Voltage Ra- tio | U16 |  | Range：1~30000 |
| 44237 | PV Storage System Meter 2 CT Ratio | U16 |  | Range：1~30000 |
| 44238 | PV Storage System Meter 2 CT Direction | U16 |  | 0: Forward (CT arrow points away from the inverter, i.e., toward the grid), 1: Reverse setting, default 0. Other values invalid. |
| 44239 | PV Storage System Meter 2 Type and In- stallation Location Set- tings | U16 |  | High byte: Meter installation loca- tion: 0x0100 – Grid‑tied inverter total output side 0x0200 – Grid load total output side Low byte: Meter type: 0x0001 – Eastron single‑phase 0x0002 – Eastron three‑phase 0x0003 – Chint split‑phase meter |

| 44240 | TCP Port Function | U16 |  | BIT00: DHCP setting – 0: Dynam- ic, 1: Static, default 0; BIT01–15: Reserved Note: Only applicable to models that support TCP port and its func- tions. |
| --- | --- | --- | --- | --- |
| 44241~ 44242 | TCP Port IP Address | U32 |  | Data Format Description: Example: If the IP address is 192.168.0.2, then register 44241 = 0xC0A8 (where 0xC0 in hex = 192 in decimal, 0xA8 in hex = 168 in decimal), and register 44242 = 0x0002 (where 0x00 in hex = 0 in decimal, 0x02 in hex = 2 in decim- al). |
| 44243~ 44244 | TCP Port Subnet Mask | U32 |  | Data format is the same as registers 44241~44242. |
| 44245~ 44246 | TCP Port Gateway | U32 |  | Data format is the same as registers 44241~44242. |
| 44247~ 44248 | TCP Port DNS Server Address | U32 |  | Data format is the same as registers 44241~44242. |
| 44249~ 44250 | TCP Port Secondary DNS Server Address | U32 |  | Data format is the same as registers 44241~44242. |
| 44251 | Modbus TCP Connec- tion Port Number Set- ting | U16 |  | Default 502 |
| 44253 | Total Grid-side Power Consumption Over‑Limit Load Dis- connect Enable | U16 |  | 0x01: Not Enabled, 0x02: Enabled, Default: Not Enabled. Other values invalid; |
| 44254 | Total Grid-side Power Consumption Over‑Limit Load Dis- connect Control | U16 |  | 0x01:smartload, 0x02: smartload & backup, Other values invalid. Default: smartload Note: Effective only when function 44253 is enabled. |
| 44255 | Generator Scheduled Maintenance Function Enable Switch | U16 |  | 0x00：Disable 0x01:Enable， Other values invalid； Default: 0x00； |
| 44256 | Generator Scheduled Maintenance Function – Interval Time | U16 | 1day | Range: 1-60day， Default: 15days |
| 44257 | Generator Scheduled Maintenance Function – | U16 | 1min | Range: 5-30min, Default:10min |

|  | Runtime |  |  |  |
| --- | --- | --- | --- | --- |
| 44258 | Generator Minimum Operating Power | U16 | 0.1kW | Range: 0–65000; Default: 24% of unit rated power. |
| 44268 | TCP Port MAC Address Byte 1 & 2 | U16 |  | Low byte represents the 1st byte, high byte represents the 2nd byte. Example: If the MAC address is 0x00-0x80-0xE1-0x00-0x01-0x02, then the value of this register is 0x8000. |
| 44269 | TCP Port MAC Address Byte 3 & 4 | U16 |  | Low byte represents the 3rd byte, high byte represents the 4th byte. Example: If the MAC address is 0x00-0x80-0xE1-0x00-0x01-0x02, then the value of this register is 0x00E1. |
| 44270 | TCP Port MAC Address Byte 5 & 6 | U16 |  | Low byte represents the 5th byte, high byte represents the 6th byte. Example: If the MAC address is 0x00-0x80-0xE1-0x00-0x01-0x02, then the value of this register is 0x0201. |
| 44275 | DRM Mode 2 Logic Interface S1 Public Grid-Side Power Feed-in Limit Value 1 | U16 | 0.01% | Range: 0~100%, default 0% |
| 44276 | DRM Mode 2 Logic Interface S2 Public Grid-Side Power Feed-in Limit Value 2 | U16 | 0.01% | Range: 0~100%, default 30% |
| 44277 | DRM Mode 2 Logic Interface S3 Public Grid-Side Power Feed-in Limit Value 3 | U16 | 0.01% | Range: 0~100%, default 60% |
| 44278~ 44279 | DRM Mode 2 Logic Interface S4 Grid-to-Battery Charg- ing Power Limit Value | U32 | 1W | Standalone range: 0~Pn Parallel range: 0~(Pn × number of parallel units) Default: 4.2 kW |
| 44280 | Remote Active Power Control Port Selection Command | U16 |  | BIT00~BIT03: Power Control Port Selection - disabled, - reserved, - enable remote control on the AC Grid Port - reserved, |

|  |  |  |  | 4 enable remote control on the Bat- tery Port 5~15 invalid BIT04~BIT07: PV Control 0 invalid（Default） 1 PV shutdown BIT08~BIT15: reserved Note: If no valid command "2" or AC active power command or battery power command is received within a specified time period, this register will revert to 0. The "specified time" is defined by register 43282, with a default of 5 minutes. |
| --- | --- | --- | --- | --- |
| 44281 | Remote Reactive Power Control Port Selection Command | U16 |  | BIT00~BIT03:Reactive Power Control Port Selection 0 disabled, 1 reserved, 2 enable remote control on the AC Reactive Power Grid Port 3 reserved, 4~15 invalid BIT13~BIT15: reserved Note: If no valid command "2" is received within a specified time period, this register will revert to 0. The "speci- fied time" is defined by register 43282, with a default of 5 minutes. |
| 44282~ 44283 | Power Control Battery Power Value | S32 | 1W | +: charge battery -: discharge battery |
| 44284~ 44285 | Power Control AC Power Value | S32 | 1W | +: export to grid -: import from grid |
| 44286~ 44287 | Power Control Reactive Power Value | S32 | 1Var | +: Inductive reactive power (lag- ging, absorbed by the load) -: capacitive reactive power (lead- ing, supplied to the load) |

- Protocol Usage Example

Taking the energy storage inverter with communication address 1 as an example, the com- munication data is in Hexadecimal (Hex) format.

  - Reading Operational Information

- Obtain the Main DSP Firmware Version Information

The host computer reads register address 33001 and takes the low-order byte as the major version number, and reads register address 33021 and takes the low-order byte as the minor ver- sion number. Example communication data:

Host computer sends: 01 04 80 E9 00 01 C9 FE，Inverter replies: 01 04 02 00 0D 78 F5

Host computer sends: 01 04 80 FD 00 01 89 FA，Inverter replies: 01 04 02 00 05 79 33 Based on the operational logic and the data above, and referring to the corresponding register

"Description," the Main DSP Firmware Version is determined to be "0D05".

- Obtain the Energy Storage Inverter Serial Number (SN)

Corresponding to register addresses 33004~33019. Example communication data: Host computer sends: 01 04 80 EC 00 10 19 F3，

Inverter replies: 01 04 20 31 30 33 31 37 33 30 32 35 34 33 30 30 38 38 34 00 00 00 00 00

00 00 00 00 00 00 00 00 00 00 00 A0 7A

Based on the corresponding register "Description," the Serial Number (SN) is “1031730254300884”.

- Obtain the Over-Discharge SOC Setting Parameter

Corresponding to register address 43011. Example communication data:

Host computer sends: 01 03 A8 03 00 01 54 6A，Inverter replies: 01 03 02 00 14 B8 4B Based on the corresponding register "Description," the Over-Discharge SOC setting value

is 20%.

  - Setting Operational Parameters

- Power On

Corresponding to register address 43007. Example communication data:

Host computer sends: 01 06 A7 FF 00 BE 1A FE，Inverter replies: 01 06 A7 FF 00 BE 1A FE

- Set Date and Time

Set the date and time to "January 6, 2026, 17:31:30". Corresponding to register addresses 43000~43005. Example communication data:

Host computer sends: 01 10 A7 F8 00 06 0C 00 1A 00 01 00 06 00 11 00 1F 00 1E D0 03

Inverter replies: 01 10 A7 F8 00 06 E2 8E

- Appendix

  - Appendix 1（M35000）

| Register Value （M:35000） | Inverter Model | Remarks |
| --- | --- | --- |
| 0x0000 | / | Undefined |
| 0x2030 | 5G/S5 Series Single-Phase Low-Voltage Battery Energy Storage Unit | / |
| 0x2031 | 5G/S5 Series Single-Phase AC-Coupled | / |
| 0x2060 | 5G Series Three-Phase High-Voltage Battery Energy Storage Unit | / |
| 0x2070 | S6 Series Three-Phase High-Voltage Battery 5-12kW Energy Storage Unit | / |
| 0x2071/0x2171 | S6 Series Three-Phase High-Voltage Battery 12-20kW Energy Storage Unit | / |
| 0x2172 | S6 Series Three-Phase Low-Voltage Bat- tery 10-15kW Energy Storage Unit | / |
| 0x2073/0x2173/0x2273 | S6 Series Three-Phase High-Voltage Battery 50kW Energy Storage Unit | / |
| 0x2074 | S6 Series Three-Phase High-Voltage 5-10kW AC-Coupled Pro |  |
| 0x2080 | S6 Series Single-Phase High-Voltage Battery US Version Energy Storage Unit | / |
| 0x2181 | S6 Series Single-Phase Low-Voltage Battery 12-16kW US Version Energy Storage Unit | / |
| 0x2183 | S6 Series Low-Voltage Battery 5-8kW Brazil Split-Phase Energy Storage Unit |  |
| 0x2090/0x2190 | S6 Series Single-Phase Low-Voltage Battery 3-18kW Energy Storage Unit | \ |
| 0x2091 | S6 Series Single-Phase Low-Voltage Battery AC-Coupled | \ |
| 0x3010 | S5 Series Single-Phase Low-Voltage Battery Off-Grid Energy Storage Unit | \ |
| 0x3020/0x3120 | S6 Series Single-Phase Low-Voltage Battery Off-Grid Energy Storage Unit | \ |

  - Appendix 2（M33092）

| Register Value | National Standard |  |
| --- | --- | --- |
| （M:33092） | Three-Phase Energy Storage | Single-Phase Energy Storage |
| 01H | G59/3 | G59/3 |
| 02H | UL480-13(60Hz480V) (Specification: Low-Voltage, 60Hz, 270V) | UL240-13 |
| 03H | VDE0126(380V) | VDE0126 |
| 04H | Reserve | Reserve |
| 05H | Reserve | Reserve |
| 06H | CQC-380A | CQC（B） |
| 07H | EN50438IE | EN50438IE |
| 08H | UL-380V(60Hz380V) Note: Low-Voltage UL-220V(60Hz220V) | UL-208V |
| 09H | MEX-CFE | MEX-CFE |
| 0AH | User-Defined | User-Defined |
| 0BH | VDE4105(380V) | VDE4105 |
| 0CH | DK1 | DK1 |
| 0DH | EN50549PO | EN50549PO |
| 0EH | EN50549NL | EN50549NL |
| 0FH | EN50549ES(Estonia) | EN50549ES |
| 10H | EN50438L | EN50438L |
| 11H | UL-480V-A | UL-240V-A |
| 12H | UL-380V-A | UL-208V-A |
| 13H | BRAZIL | BRAZIL |
| 14H | Reserve | Reserve |
| 15H | Reserve | Reserve |
| 16H | G83/1 | G83/1 |
| 17H | RD1699 | RD1699 |
| 18H | IEC61727 | IEC61727 |
| 19H | GN-380L | G83/1-A |
| 1AH | CQC-480A | GNB |
| 1BH | GN-HV-L | GNC |
| 1CH | G59/3-A | NewZeal |
| 1DH | 4105/480(480V) | G83/3 |
| 1EH | Reserve | Chile |
| 1FH | NewZeal | NRS097 |
| 20H | Reserve | Philippin |
| 21H | CQC-540A | N4105-BEL |
| 22H | GN-540L | IEC61727L |
| 23H | N4105-BEL | KS1 |

| 24H | CHILE | France |
| --- | --- | --- |
| 25H | NRS097 | ISONE240 |
| 26H | GN380L-A | ISONE208 |
| 27H | GNHVL-A | ISONE240A |
| 28H | NRS480 | ISONE208A |
| 29H | CQC380DZ | GN300V |
| 2AH | GN380DZL | MEA(THAILAND) |
| 2BH | ISONE480 | R21P3-240 |
| 2CH | ISONE480A | R21P3-208 |
| 2DH | KS1 | R21P3-24A |
| 2EH | R21P3-480 | R21P3-20A |
| 2FH | R21P3-48A | Sri Lanka |
| 30H | Philippin | PEA(THAILAND) |
| 31H | France | Reserve |
| 32H | Sri Lanka | Mala230LV |
| 33H | MEA | Indon230V |
| 34H | PEA | G98 |
| 35H | Mala230MV | G99 |
| 36H | Mala230LV | GEN50 |
| 37H | Mala277LV | GEN60 |
| 38H | Mala277MV | TW220(TAIWAN) |
| 39H | Indon230V | TW110(TAIWAN) |
| 3AH | Dubai-A(Dubai Medium Voltage) | DK230V |
| 3BH | Dubai-B(Dubai Low Voltage) | Barbados |
| 3CH | DEWA277MV | BRAZIL-H |
| 3DH | G98 | G99-N |
| 3EH | G99 | CEI 0-21(Italy) |
| 3FH | BDEW230V | MEX-220V (MEX-110V Note: Low-Voltage Dis- play) |
| 40H | BDEW277V | MEX220-A (MEX110-A Note: Low-Voltage Dis- play) |
| 41H | GEN50 | SG1 |
| 42H | GEN60 | Reserve |
| 43H | Reserve | Reserve |
| 44H | KS2(South Korea Non-Standard) | EN50549 |
| 45H | TW220(TAIWAN) | PH-L(Philippin) |
| 46H | DK277V | C10/11(Belgium) |
| 47H | DK230V | DK2 |
| 48H | Barbados | G98-NI |
| 49H | IEC61727L | G99-NI |
| 4AH | SG1（Singapore） | IRAN(Iran) |

| 4BH | G99N | EIFS-SW(Sweden) |
| --- | --- | --- |
| 4CH | MEX-480V (MEX-220V Note: Low-Voltage Dis- play) | R14-240A（Hawaii） |
| 4DH | MEX480V-A (MEX220V-A Note: Low-Voltage Display) | R14-208A（Hawaii） |
| 4EH | Reserve | TOR(Austria) |
| 4FH | Reserve | R14-240（Hawaii） |
| 50H | Reserve | R14-208（Hawaii） |
| 51H | Reserve | Reserve |
| 52H | EN50549 | GREECE (Greece) |
| 53H | CEI 0-21(Italy) | HK220(Hong Kong) |
| 54H | PH-L(Philippin) | RENBLAD(Norway 342) |
| 55H | C10/11(Belgium) | 4777-A (AS4777-2020A) |
| 56H | DK2 | 4777-B |
| 57H | G98-NI | 4777-C |
| 58H | G99-NI | 4777-N (New Zealand) |
| 59H | IRAN(Iran) | NTS631 |
| 5AH | EIFS-SW(Sweden) | UL-240-18 (Note: UL-1574 Requirements A refers to the older standard UL 1547-2014. A2 refers to the newer standard UL 1547-2018.) |
| 5BH | KS3 | UL-208-18 |
| 5CH | TOR(Austria) | EN50549IE |
| 5DH | BRAZIL-H | VIETNAM |
| 5EH | Reserve | Reserve |
| 5FH | Reserve | PN-50549 (Poland) |
| 60H | Reserve | ESB-Micro (Note: New Ireland EN50549) |
| 61H | G99-B | ESB-Mini (Note: New Ireland EN50549) |
| 62H | Reserve | Israel(Israel) |
| 63H | Reserve | R14H-240（Hawaii） |
| 64H | GREECE | R14H-208（Hawaii） |
| 65H | HK220(Hong Kong) | EN50549FI(Finland) |
| 66H | REN342(RENBLAD Norway 342) | BRA-N220 (BRA-N22L |

|  |  | Note: Low-Voltage Display) |
| --- | --- | --- |
| 67H | CEI 0-16 | EN50549TR(土耳其 50549-1) |
| 68H | NTS631 | MEX-22N |
| 69H | 4777-A (AS477-2020) | LTU-1 (Lithuania 50549-1) |
| 6AH | 4777-B | GNHN(For Henan Grid) |
| 6BH | 4777-C | ES-L-N（Spain） |
| 6CH | 4777-N(NEW ZEALAND) | MEX-CFE-SP(Split-Phase Grid) |
| 6DH | 4777-A-H | JAM-230(Jamaica) |
| 6EH | 4777-B-H | Custom50（Specification: For 50Hz Grid） |
| 6FH | 4777-C-H | Custom60（Specification: For 50Hz Grid） |
| 70H | 4777-N-H | Reserve |
| 71H | UL480-18 (Note: UL-1574 Requirements A refers to the older standard UL 1547-2014. A2 refers to the newer standard UL 1547-2018.) | HUN-1 (Hungarian standards) |
| 72H | EN50549IE | LUMA-240（Puerto Rico_ODM） |
| 73H | EN50549-2 | Czech（Czech） |
| 74H | VIETNAM | R21-208 |
| 75H | VDE4110 | R21-240 |
| 76H | GNSD-A380 | SI-1 |
| 77H | GNSD-A-HV | NA-EEA（Switzerland） |
| 78H | GNSD-A540 | Qatar(Qatar) |
| 79H | GNSD-B380 | CYP(Cyprus) |
| 7AH | GNSD-B-HV | ROU（Romania） |
| 7BH | GNSD-B540 | Egypt（Egypt） |
| 7CH | PN-50549(Poland) | Reserve |
| 7DH | ESB-Micro | Reserve |
| 7EH | ESB-Mini | Reserve |
| 7FH | Israel(Israel) | Reserve |
| 80H | Egypt (Egypt) | Reserve |
| 81H | KS3-LVRT | Reserve |
| 82H | CQC3310 | Reserve |
| 83H | EN50549FI(Finland) | Reserve |
| 84H | BRA-N380 (BRA-N38L Note: Low-Voltage Dis- play) | Reserve |
| 85H | EN50549TR(Turkey 50549-1) | Reserve |
| 86H | TR-2(Turkey 50549-2) | Reserve |

| 87H | SI-1（Slovenia 50549-1） | Reserve |
| --- | --- | --- |
| 88H | SI-2（Slovenia 50549-2） | Reserve |
| 89H | PH-480(Philippines High Voltage) | Reserve |
| 8AH | VN-480（Vietnam High Voltage） | Reserve |
| 8BH | LTU-1(Lithuania 50549-1) | Reserve |
| 8CH | LTU-2(Lithuania 50549-2) | Reserve |
| 8DH | Reserve | Reserve |
| 8EH | Reserve | Reserve |
| 8FH | MEX-48N(MEX-22N Note: Low-Voltage Display) | Reserve |
| 90H | Reserve | Reserve |
| 91H | Reserve | Reserve |
| 92H | Reserve | Reserve |
| 93H | Reserve | Reserve |
| 94H | Reserve | Reserve |
| 95H | Reserve | Reserve |
| 96H | Reserve | Reserve |
| 97H | Reserve | Reserve |
| 98H | Reserve | Reserve |
| 99H | Reserve | Reserve |
| 9AH | Reserve | Reserve |
| 9BH | Reserve | Reserve |
| 9CH | ES-L-N（Spain） | Reserve |
| 9DH | DK1-L-400 | Reserve |
| 9EH | DK2-L-400 | Reserve |
| 9FH | DK1-M-400 | Reserve |
| A0H | DK2-M-400 | Reserve |
| A1H | TOR-MV(Austria) | Reserve |
| A2H | Czech （Specification: For Czech 2023 A1/A2） | Reserve |
| A3H | Reserve | Reserve |
| A4H | Reserve | Reserve |
| A5H | Reserve | Reserve |
| A6H | Reserve | Reserve |
| A7H | Reserve | Reserve |
| A8H | G99 NI-B | Reserve |
| A9H | HUN(Hungary) | Reserve |
| AAH | FI-1(Finnish standards) | Reserve |
| ABH | IEC61727H(Indian High-Voltage standards) | Reserve |
| ACH | Reserve | Reserve |
| ADH | Reserve | Reserve |

| AEH | BRAZIL-HV (For 125K-HV) | Reserve |
| --- | --- | --- |
| AFH | Czech-MV （Czech） | Reserve |
| B0H | Custom50（Specification: For 50Hz Grid） | Reserve |
| B1H | Custom60（Specification: For 50Hz Grid） | Reserve |
| B2H | G29319-38 | Reserve |
| B3H | G29319-48 | Reserve |
| B4H | G29319-54 | Reserve |
| B5H | G19964-38 | Reserve |
| B6H | G19964-48 | Reserve |
| B7H | G19964-54 | Reserve |
| B8H | Qatar | Reserve |
| B9H | R21-208 | Reserve |
| BAH | R21-240 | Reserve |
| BBH | R21-480 | Reserve |
| BCH | Bra-480(Brazil Old Standard) | Reserve |
| BDH | NA-EEA-A（Switzerland） | Reserve |
| BEH | NA-EEA-B（Switzerland） | Reserve |
| BFH | SriLankaN | Reserve |
| C0H | PH-L-480 | Reserve |
| C1H | ISR-M(Israel Medium-Voltage Grid) | Reserve |
| C2H | CYP-230(Cyprus) | Reserve |
| C3H | POL-M-400(Poland Medium-Voltage Standards) | Reserve |
| C4H | PH-M-380(Philippines Me- dium-Voltage) | Reserve |
| C5H | ROU-380（Romania） | Reserve |
| C6H | G10186（New National Standard） | Reserve |
| 100H | MEX-220V(Note: Low-Voltage Dis- play) | Reserve |
| 101H | MEX220V-A(Note: Low-Voltage Dis- play) | Reserve |
| 102H | MEX-22N(Note: Low-Voltage Dis- play) | Reserve |

  - Appendix 3（M33095）

| Register Value (M:33095(33070)) | Inverter Chinese Display | Inverter English Display |
| --- | --- | --- |
| 0000H（0000） | 等待状态 | Waiting |
| 0000H（0001） | 控制离网 | Grid Off |
| 0000H（0002） | 等待状态 01 | Waiting01 |
| 0001H | 开环运行 | OpenRun |
| 0002H | 软起运行 | SoftRun |
| 0003H（0000） | 并网运行 | Generating |
| 0003H（xx01） | 过温限载 | LimByTemp |
| 0003H（xx02） | 过频限载 | LimByFreq |
| 0003H（xx04） | 过压限载 | LimByVg |
| 0003H（xx08） | 无功限载 | LimByVar |
| 0003H（xx10） | 欠频限载 | LimByUnFr |
| 0003H（xx20） | 功率软起 | Ramp-up |
| 0003H（xx40） | 有旁路过载 | Overload |
| 0003H（xx80） | 交流端子过温限载 | LimByACTemp |
| 0003H（01xx） | DRM 限载 | LimByDRM |
| 0003H（02xx） | PLMT 限载 | LimByEPM |
| 0004H | 离网运行 | Off-Grid |
| ………… | ………… | ………… |
| F010H | 电网浪涌 | Surge Alarm |
| F011H | 风扇故障(内部风扇) | Fan Alarm |
| F013H | 电网防雷异常 | VgSpdFail |
| F014H | 直流防雷异常 | DcSpdFail |
| F015H | 风扇故障(外部风扇) | Fan_H Alarm |
| F016H | 熔丝异常 | FuseFail |
| F017H | 相线接地告警 | L&PE FAIL |
| F019H(0000) | 0000_Boost 异常 | 0000_BoostFail |
| F01AH | 发电机启动异常 | Gen_Start_Fail |
| F01BH | 发电机停止异常 | Gen_Stop_Fail |
| F01CH | IGBT 温度差异 | IGBT TEMP DIF |
| F01DH | 零地电压异常 | N-PE V fault |
| F01EH | PV 与电池功率不匹配 | PV-Batt-Mismatch |
| F01FH | 发电机电压相位异常 | Gen-Phase-Err |
| ………… | ………… | ………… |
| F020H | 电池告警（警示）01 | BMS_ALARM(WARN)01 |
| F021H | 电池告警（警示）02 | BMS_ALARM(WARN)02 |
| F022H | 电池告警（警示）03 | BMS_ALARM(WARN)03 |
| F023H | 电池告警（警示）04 | BMS_ALARM(WARN)04 |
| F024H | 电池告警（警示）05 | BMS_ALARM(WARN)05 |
| F025H | 电池告警（警示）06 | BMS_ALARM(WARN)06 |

| F026H | 电池告警（警示）07 | BMS_ALARM(WARN)07 |
| --- | --- | --- |
| F027H | 电池告警（警示）08 | BMS_ALARM(WARN)08 |
| F028H | 电池告警（警示）09 | BMS_ALARM(WARN)09 |
| F029H | 电池告警（警示）10 | BMS_ALARM(WARN)10 |
| F02AH | 电池告警（警示）11 | BMS_ALARM(WARN)11 |
| F02BH | 电池告警（警示）12 | BMS_ALARM(WARN)12 |
| F02CH | 电池告警（警示）13 | BMS_ALARM(WARN)13 |
| F02DH | 电池告警（警示）14 | BMS_ALARM(WARN)14 |
| ………… | ………… | ………… |
| F035H | AC Coupling 锁定 | AC Coupling Lock |
| F036H | AC Coupling 暂停 | AC Coupling Stop |
| F037H | Backup 断路器过载 | BK-CB-Ovload |
| ………… | ………… | ………… |
| F040H | CT 方向告警 | CT_Dir Fail |
| F041H | 电表相序告警 | MET_LINE WARN |
| F042H | 从机相序告警 | SLV_LINE WARN |
| ………… | ………… | ………… |
| F050H | 电网电压不平衡告警 | GRID_VOLT_UNBALANCE_WARNING |
| F051H | 直流开关异常告警 | DC_SWITCH_ABNORMAL_WARNING |
| ………… | ………… | ………… |
| F080H | 并网逆变器通讯失败 | PVInv-ComFail |
| F081H | 电表 2 异常告警 | Meter2-Fail |
| F082H | 并机主从机软件版本不一 致 | Par-Ver-Mismatch |
| F083H | 卸载(说明：总网侧取电超 限负载断开) | Load-CutOff |
| F084H | 卸载锁定 | Load-CutOff-Lock |
| ………… | ………… | ………… |
| 1010H(0000) | 电网过压 | OV-G-V |
| 1010H(0001) | 电网过压 01 | OV-G-V01 |
| 1010H(0002) | 电网过压 02 | OV-G-V02 |
| 1010H(0003) | 电网过压 03 | OV-G-V03 |
| 1010H(0004) | 电网过压 04 | OV-G-V04 |
| 1010H(0005) | 电网过压 05 | OV-G-V05 |
| 1011H(0000) | 电网欠压 | UN-G-V |
| 1011H(0001) | 电网欠压 01 | UN-G-V01 |
| 1011H(0002) | 电网欠压 02 | UN-G-V02 |
| 1012H(0000) | 电网过频 | OV-G-F |
| 1012H(0001) | 电网过频 01 | OV-G-F01 |
| 1012H(0002) | 电网过频 02 | OV-G-F02 |
| 1013H(0000) | 电网欠频 | UN-G-F |
| 1013H(0001) | 电网欠频 01 | UN-G-F01 |

| 1013H(0002) | 电网欠频 02 | UN-G-F02 |
| --- | --- | --- |
| 1014H | 电网逆流 | Backfeed_Iac |
| 1015H | 无电网 | NO-Grid |
| 1016H | 电网不平衡 | G-PHASE |
| 1017H | 电网频率抖动 | G-F-FLU |
| 1018H | 电网过流 | OV-G-I |
| 1019H | 电网电流跟踪故障 | IGFOL-F |
| 101AH | 电网相位异常 | PHASE-FAULT |
| 101CH | 过流筛选故障 | IGBTSift-Pro |
| 101DH(0001) | 静态 1 级过压 | G100-VH |
| 101DH(0002) | 静态 2 级过压 | G100-OV1 |
| 101DH(0003) | 动态过压 | G100-D-VH |
| 101DH(0004) | 静态 1 级欠压 | G100-UV1 |
| 101DH(0005) | 静态 2 级欠压 | G100-VL |
| 101DH(0006) | 动态欠压 | G100-D-VL |
| 101EH | 电网波动异常 | GV-F |
| ………… | ………… | ………… |
| 1020H(0000) | 直流过压 | OV-DC |
| 1020H(0001) | 直流过压 01 | OV-DC01 |
| 1020H(0002) | 直流过压 02 | OV-DC02 |
| 1020H(0003) | PV 接地故障 | PVGndRun Fau |
| 1020H(0004) | DCBoost 故障 | BoostFail |
| 1021H | 直流母线过压 | OV-BUS |
| 1022H | 直流母线不均压 | UNB-BUS |
| 1023H(0000) | 直流母线欠压 | UN-BUS |
| 1023H(0001) | 直流母线欠压 01 | UN-BUS01 |
| 1023H(0002) | 直流母线欠压 02 | UN-BUS02 |
| 1024H | 直流母线不均压 2 | UNB2-BUS |
| 1025H | 直流A 路过流 | OV-DCA-I |
| 1026H | 直流B 路过流 | OV-DCB-I |
| 1027H | 直流输入扰动 | DC-INTF. |
| 1028H | 直流反接故障 | Reve-DC |
| 1029H | PV 中点接地故障 | PvMidIso |
| 102AH | 母线电压不一致 | Vbus-Sam |
| 102BH | PV 端口浪涌 | PV Surge |
| 102CH | 直流过温故障 | OV-TEM05 |
| 102DH | MPPT 过压故障 | OV-MPPT |
| 102EH | MPPT 过流故障 | OC-MPPT |
| ………… | ………… | ………… |
| 1030H | 电网扰动 | GRID-INTF. |
| 1031H | DSP 初始化保护 | INI-FAULT |
| 1032H | 过温保护 | OV-TEM01 |
| 1033H(0000) | PV 绝缘故障 | PV ISO-PRO |

| 1033H(0001) | PV 绝缘故障 01 | PV ISO-PRO1 |
| --- | --- | --- |
| 1033H(0002) | PV 绝缘故障 02 | PV ISO-PRO2 |
| 1034H(0000) | 漏电流保护 | ILeak-PRO |
| 1034H(0001) | 漏电流保护 01 | ILeak-PRO01 |
| 1034H(0002) | 漏电流保护 02 | ILeak-PRO02 |
| 1034H(0003) | 漏电流保护 03 | ILeak-PRO03 |
| 1034H(0004) | 漏电流保护 04 | ILeak-PRO04 |
| 1035H | Relay 检测保护 | RelayChk-FAIL |
| 1036H(0000) | DSP_B 通讯异常 | DSP-B-Com-Fau |
| 1036H(0001) | DSP_B 采样异常 | DSP-B-Sam-Fau |
| 1037H | 直流分量过大 | DCInj-FAULT |
| 1038H | 12V 欠压保护 | 12Power-FAULT |
| 1039H | 漏电流自检保护 | ILeak-Check |
| 103AH | 欠温保护 | UN-TEM |
| 103BH | IGBT 温度差异 | IGBT TEMP DIF |
| 103CH | 二级电网扰动 | GRID-DIST.02 |
| 103DH | 相线接地告警 | L&PE-FAULT |
| 103EH | NTC 过温保护 | OV-TEM02 |
| 103FH | AC 端子过温故障 | OV-TEM03 |
| ………… | ………… | ………… |
| 1040H | 电弧自检保护 | AFCI-Check |
| 1041H | 电弧保护 | ARC- FAULT |
| 1046H | 电网扰动 02 | GRID-INTF02 |
| 1047H | 电网电流采样异常 | IG-AD |
| 1048H | 电网三级过压 | OV03-G-V |
| ………… | ………… | ………… |
| 1050H | 网侧电流瞬时过流 | OV-IgTr |
| 1051H | 直流母线硬件过压 | OV-BUS-H |
| 1052H | LLC 硬件过流 | OV-ILLC |
| 1053H | 硬限制故障 | EPM-HardLimit |
| 1057H | 负载过载故障 | Over-Load |
| 1058H | DSP 自检异常 | DspSelfChk |
| 1059H | Vg 采样异常 | Vg-Sample |
| 105AH | DSP 硬件不匹配 | HardFault |
| 105DH | 直流母线硬件过压(储能) | OV-BUS-H(Energy Storage Unit) |
| ………… | ………… | ………… |
| 1800H(0000) | 直流平均值过流 | OV-DC-I |
| 1800H(0005) | 直流 5 路平均值过流 | OV-DC05-I |
| 1800H(0006) | 直流 6 路平均值过流 | OV-DC06-I |
| 1800H(0007) | 直流 7 路平均值过流 | OV-DC07-I |
| 1800H(0008) | 直流 8 路平均值过流 | OV-DC08-I |
| 1800H(0009) | 直流 9 路平均值过流 | OV-DC09-I |
| 1800H(000A) | 直流 10 路平均值过流 | OV-DC10-I |

| 1801H(0000) | 直流输入过压 | OV-DC |
| --- | --- | --- |
| 1801H(0005) | 直流 5 输入过压 | OV-DC05 |
| 1801H(0006) | 直流 6 输入过压 | OV-DC06 |
| 1801H(0007) | 直流 7 输入过压 | OV-DC07 |
| 1801H(0008) | 直流 8 输入过压 | OV-DC08 |
| 1801H(0009) | 直流 9 输入过压 | OV-DC09 |
| 1801H(000A) | 直流 10 输入过压 | OV-DC10 |
| ………… | ………… | ………… |
| 2010H/2011H | Fail Safe | Fail Safe |
| 2012H | 电池通讯故障 | Batt_Comm_FAIL |
| 2014H | DSP 通讯故障 | DSP_Comm_FAIL |
| 2018H | DRM 连接失败 | DRM_LINK_FAIL |
| 201AH | CT 连接异常 | CT_FAULT |
| 201BH | DRM 控制离网 | DRM_CTL_Off |
| ………… | ………… | ………… |
| 2040H | EPM 硬限制保护 | EPM-HardLimit |
| 2041H | AFCI 板通讯异常 | AFCI-Comm-Fail |
| 2042H | AFCI 板CT 模组硬件异常 | AFCI-CTModule-Fail |
| 2043H | G100 过流保护 | State 2 excursion |
| 2044H | 多主机设置异常 | MulMaster-Set-Err |
| 2045H | SPH 通信异常 | SPH-Comm-Fail |
| 2046H | 并机从机通信异常 (从机未接收到主机数据) | Slv-Comm-Err |
| 2047H | 配电盘过流 | Panel Ov-C |
| 2048H | 电池低电量(离网状态下) | Low Battery |
| 204AH | 逆变器桥口硬限制保护 | Inv-HardLimit |
| 204BH | G100 电表通信故障 | G100-ComFail |
| 204CH | G100 CT 故障 | G100-CTFault |
| 204DH | AFCI 板类型不匹配 | AFCI_Mismatch |
| ………… | ………… | ………… |
| 2804H | 电池 1 接线匹配异常。 | Batt1-Wire-Err |
| 2805H | 电池 2 接线匹配异常。 | Batt2-Wire-Err |

  - Appendix 4：Status Bit Definitions

| Register Address | Type | BIT Po- sition | Fault Status | Status Code |
| --- | --- | --- | --- | --- |
| 33121 | Working Status Bit Definitions | BIT00 | Normal Operation (Device Status / Overall Operating Status) | 0— No 1—YES |
|  |  | BIT01 | Initial Standby (Device Status) | 0— No 1—YES |
|  |  | BIT02 | Shutdown | 0— No 1—YES |
|  |  | BIT03 | Fault (Device Fault Status / Overall Operating Status) | 0— No 1—YES |
|  |  | BIT04 | Standby (Device Status) | 0— No 1—YES |
|  |  | BIT05 | Derated Operation (due to temperature, frequency, etc.) | 0— No 1—YES |
|  |  | BIT06 | Limited Power Operation (due to external factors) | 0— No 1—YES |
|  |  | BIT07 | Bypass Overload | 0— No 1—YES |
|  |  | BIT08 | Load Fault (Load Normalcy Status) | - — Normal - — Fault |
|  |  | BIT09 | Grid Fault (Grid Normalcy Status) | - — Normal - — Fault |
|  |  | BIT10 | Battery Fault (Battery Nor- malcy Status) | - — Normal - — Fault |
|  |  | BIT11 | Reserve | 0— No 1—YES |
|  |  | BIT12 | Grid Surge (Combined with register 33339 to form Inverter Warn- ing) | 0— No 1—YES |
|  |  | BIT13 | Fan Fault (Combined with register 33339 to form Inverter Warn- ing) | 0— No 1—YES |
|  |  | BIT14 | External Fan Fault (Combined with register 33339 to form Inverter Warn- ing) | 0— No 1—YES |
|  |  | BIT15 | Fault Shutdown | 0—No 1—YES |
| 33339 | Inverter Warning | BIT00 | Generator Start-up Abnormal / Generator Start Failure | 0—Normal 1—Alarm |
|  |  | BIT01 | Generator Stop Abnormal / Generator Stop Failure | 0—Normal 1—Alarm |
|  |  | BIT02 | PV and Battery Power Mis- match | 0—Normal 1—Alarm |
|  |  | BIT03 | Generator Voltage/Phase Ab- | 0—Normal |

|  |  |  | normality | 1—Alarm |
| --- | --- | --- | --- | --- |
|  |  | BIT04 | SolisHub-DSP Communica- tion Fault | 0—Normal 1—Alarm |
|  |  | BIT05 | AC-Coupling Locked | 0—Normal 1—Alarm |
|  |  | BIT06 | AC-Coupling Suspended | 0—Normal 1—Alarm |
|  |  | BIT07 | Backup Circuit Breaker Over- load | 0—Normal 1—Alarm |
|  |  | BIT08 | Grid-Tied Inverter Communi- cation Failure | 0—Normal 1—Alarm |
|  |  | BIT09 | Energy Meter 2 Abnormality Alarm | 0—Normal 1—Alarm |
|  |  | BIT10 | Master/Slave Software Version Incompatibility | 0—Normal 1—Alarm |
|  |  | BIT11 | Unload (Total Grid-Side Pow- er Draw Exceeds Limit, Load Disconnected) | 0—Normal 1—Alarm |
|  |  | BIT12 | Unload Locked (Total Grid-Side Power Draw Ex- ceeds Limit, Load Discon- nected) | 0—Normal 1—Alarm |
|  |  | BIT13 | Reserve | \ |
|  |  | BIT14 | Reserve | \ |
|  |  | BIT15 | Reserve | \ |
|  |  | BIT02 | Reserve | 0— No 1—YES |

  - Appendix 5：Low-Voltage Battery Number

| No. | Register 43009 | Battery Type | Remarks |
| --- | --- | --- | --- |
| 1 | 0x0000 | No Battery |  |
| 2 | 0x0001 | PYLON_LV (PYLON Low-Voltage Battery) |  |
| 3 | 0x0002 | Reserve |  |
| 4 | 0x0003 | B_BOX_LV (BYD Low-Voltage Battery) |  |
| 5 | 0x0004 | Dyness LV | (For S5 AC-Coupled, 0x0004 indicates LG Low-Voltage Battery) |
| 6 | 0x0005 | PureDrive Low-Voltage Battery |  |
| 7 | 0x0006 | LG Chem LV LG Low-Voltage Battery | (For S5 AC-Coupled, 0x0006 indicates Dy- ness Low-Voltage Battery) |
| 8 | 0x0007 | AoBo Low-Voltage Battery |  |
| 9 | 0x0008 | JiaWei Low-Voltage Battery |  |
| 10 | 0x0009 | WECO Low-Voltage Battery |  |
| 11 | 0x000A | FreedomWon Low-Voltage Battery |  |
| 12 | 0x000B | Soluna Low-Voltage Battery |  |
| 13 | 0x000C | GSL Low-Voltage Battery |  |
| 14 | 0x000D | Rita Low-Voltage Battery |  |
| 15 | 0x000E | GS Energy Risen Low-Voltage Battery |  |
| 16 | 0x000F | Alpha LV Watt |  |
| 17 | 0x0010 | UZ ENERGY CATL |  |
| 18 | 0x0011 | ATL Low-Voltage Battery |  |
| 19 | 0x0012 | Zeta Low-Voltage Battery |  |
| 20 | 0x0013 | Highstar Low-Voltage Battery |  |
| 21 | 0x0014 | KODAK Low-Voltage Battery |  |
| 22 | 0x0015 | FOX Low-Voltage Battery |  |
| 23 | 0x0016 | EXIDE Low-Voltage Battery |  |
| 24 | 0x0017 | HD Energy Low-Voltage Battery |  |
| 25 | 0x0018 | Pytes Low-Voltage Battery |  |
| 26 | 0x0019 | ARVIO Low-Voltage Battery |  |
| 27 | 0x001A | PAND Low-Voltage Battery |  |
| 28 | 0x001B | WANKE Low-Voltage Battery |  |
| 29 | 0x001C | Dowell Low-Voltage Battery |  |
| 30 | 0x001D | ROSEN ESS Rongsheng Battery |  |
| 31 | 0x001E | ZRGP ZHONGRUI LVNENG Low-Voltage Battery |  |
| 32 | 0x001F | Narada Battery |  |
| 33 | 0x0020 | BST Low-Voltage Battery |  |
| 34 | 0x0021 | Cegasa Low-Voltage Battery |  |

| 35 | 0x0022 | Meterboost |  |
| --- | --- | --- | --- |
| 36 | 0x0023 | MOURA |  |
| 37 | 0x0024 | Tecloman Low-Voltage Battery |  |
| 38 | 0x0025 | Upower UE-H |  |
| 39 | 0x0026 | Upower UE-I |  |
| 40 | 0x0027 | SUNWODA Low-Voltage Battery |  |
| 41 | 0x0028 | CFE Low-Voltage Battery |  |
| 42 | 0x0029 | DMEGC Low-Voltage Battery |  |
| 43 | 0x002A | J-Pack-LV JA Solar Hibo Low-Voltage Bat- tery |  |
| 44 | 0x002B | HY4850 Guizhou Jiaying Low-Voltage Bat- tery |  |
| 45~62 |  | Reserve |  |
| 63~82 | 0x003E~0x0052 | 0x003E -> Greenrich 0x003F -> PYTES_LV Reserve064~081 |  |
| 83 | 0x0053 | Reserve082 |  |
| 84 | 0x0054 | JA-L JA Solar Low-Voltage Battery |  |
| 85 | 0x0055 | CLENERGY Low-Voltage Battery |  |
| 86 | 0x0056 | Solis-Alpha Low-Voltage Battery |  |
| 98 | 0x0061 | Solis Low-Voltage Battery |  |
| 99 | 0x0062 | Lithium Battery LV(RS485) |  |
| 100 | 0x0063 | General-LiBat-LV Generic Low-Voltage Li- thium Battery |  |
| 101 | 0x0064 | Lead Acid Battery |  |
| 102 | 0x0065 | 48V-LiBat-LV |  |
| 103 | 0x0066 | 51.2V-LiBat-LV |  |

  - Appendix 6：High-Voltage Battery Number

| No. | Register 43009 | Battery Type | Remarks |
| --- | --- | --- | --- |
| 1 | 0x0000 | No Battery |  |
| 2 | 0x0100 | PYLON_HV High-Voltage Battery |  |
| 3 | 0x0200 | Reserve |  |
| 4 | 0x0300 | B_BOX_HV BYD High-Voltage Battery |  |
| 5 | 0x0400 | LG_HV LG High-Voltage Battery |  |
| 6 | 0x0500 | SOLUNA_HV DLG High-Voltage Battery |  |
| 7 | 0x0600 | Dyness HV |  |
| 8 | 0x0700 | Aoboet HV |  |
| 9 | 0x0800 | WECO HV |  |
| 10 | 0x0900 | Alpha HV |  |
| 11 | 0x0A00 | GS Energy |  |
| 12 | 0x0B00 | BYD-HVS/HVM/HVL |  |
| 13 | 0x0C00 | Jinko High-Voltage Battery |  |

| 14 | 0x0D00 | FOX High-Voltage Battery |  |
| --- | --- | --- | --- |
| 15 | 0x0E00 | LG_16H High-Voltage Battery |  |
| 16 | 0x0F00 | PureDrive High-Voltage Battery |  |
| 17 | 0x1000 | UZ ENERGY High-Voltage Battery |  |
| 18 | 0x1100 | Reserve |  |
| 19 | 0x1200 | Reserve |  |
| 20 | 0x1300 | Fortress High-Voltage Battery |  |
| 21 | 0x1400 | AMPACE_HV |  |
| 22 | 0x1500 | WTS High-Voltage Battery (BYD Manufac- turer) |  |
| 23 | 0x1600 | J-PACK-HV |  |
| 24 | 0x1700 | SUNWODA HV |  |
| 25~38 |  | Reserve |  |
| 39 | 0x2600 | LG Enblock S |  |
| 40 | 0x2700 | JA-H High-Voltage Battery |  |
| 41 | 0x2800 | BMZ-HV |  |
| 42 | 0x2900 | HomeGrid High-Voltage Battery | Temporarily used for S6 Single-Phase High-Voltage US Ver- sion Energy Storage Unit |
| 43 | 0x2A00 | Greenrich High-Voltage Battery | Temporarily used for S6 Three-Phase 50kW Energy Storage Unit |
| 44 | 0x2B00 | BAT High-Voltage Battery |  |
| 45 | 0x2C00 | Gotion High-Voltage Battery | Temporarily used for S6 Three-Phase 50kW Energy Storage Unit |
| 46~98 |  | Reserve |  |
| 99 | 0x6200 | Solis High-Voltage Battery |  |
| 100 | 0x6300 | General-LiBat-HV Generic High-Voltage Li- thium Battery |  |

  - Appendix 7：Energy Storage Control Switch Status Description

|  | BIT00 | Self-Consumption Mode Switch |  |  |  |  | 0—OFF 1—ON |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | BIT01 | Optimized Revenue V1 Enable Switch |  |  |  |  | 0—OFF 1—ON |
|  | BIT02 | Off-Grid Mode Switch |  |  |  |  | 0—OFF 1—ON |
|  | BIT03 | Battery Wake-up Switch |  |  |  |  | 0-Disabled |
|  |  |  |  |  |  |  | 1-Enabled |
|  | BIT04 | Backup Battery Enable Switch |  |  |  |  | 0—OFF 1—ON |
|  | BIT05 | Allow/Disallow | Grid | Power | for | Battery | 0—Disallow |
| Energy |  | Charging |  |  |  |  | 1—Allow |
| Storage | BIT06 | Feed-in Priority Mode Switch |  |  |  |  | 0—OFF 1—ON |
| Control | BIT07 | Nighttime Battery Over-Discharge Retention |  |  |  |  | 0—OFF 1—ON |
| Switch |  | Enable Switch |  |  |  |  |  |
| Status | BIT08 | Deactivated |  |  |  |  | 0—OFF 1—ON |
|  | BIT09 | Deactivated |  |  |  |  | 0—OFF 1—ON |
|  | BIT10 | Battery Conditioning Enable Switch |  |  |  |  | 0—OFF 1—ON |
|  | BIT11 | Peak-Shaving Mode Switch |  |  |  |  | 0—OFF 1—ON |
|  | BIT12 | Reserve |  |  |  |  | 0—OFF 1—ON |
|  | BIT13 | Reserve |  |  |  |  | 0—OFF 1—ON |
|  | BIT14 | Reserve |  |  |  |  | 0—OFF 1—ON |
|  | BIT15 | Reserve |  |  |  |  | 0—OFF 1—ON |