# Communication Protocol of PV Grid-Connected String Inverters

## V1.1.53

| Version number | Date | Note |
| --- | --- | --- |
| V1.1.0 | 2016-4-11 | Initial version. Unofficial version(V1.0.13) is no longer used. |
| V1.1.1 | 2016-5-13 | modify the register address and some related content: 5039–Power limitation adjustment 5040–Reactive power adjustment |
| V1.1.2 | 2017-5-13 | Add Inverter model : SG36KTL-M, SG10KTL-M, SG12KTL-M, SG80KTL, SG80KTL-M, SG125HV |
| V1.1.3 | 2017-6-10 | Add Inverter model:SG33K3J, “Fault run” change to “Fault” Add country code: UAE, Israel, Hungary |
| V1.1.4 | 2017-6-15 | AddSG125HV the number of MPPT and combiner board information |
| V1.1.5 | 2017-6-20 | Add Inverter data point : State setting |
| V1.1.6 | 2017-7-10 | Add Inverter fault/alarm code 007/030/031/032/033 |
| V1.1.7 | 2017-8-7 | Modify the name of fault code: 003/006/014/016/019/021/022/025/026/041/042//048/049/050 |
| V1.1.8 | 2017-8-12 | Delete Inverter fault/alarm code: 051 Add Inverter fault/alarm code: 053/054/055/056/059/060 |
| V1.1.9 | 2017-9-20 | Add Inverter one working state |
| V1.1.10 | 2017-9-26 | Modify the code of JP |
| V1.1.11 | 2017-10-19 | Add Inverter fault/alarm code 564/565/580/581 |
| V1.1.12 | 2017-10-24 | Add country and region code 26/27/28/29/63/64/65/66/67/59/98 Modify fault/alarm note: “LCD” changed to “LCD or APP” |
| V1.1.13 | 2017-11-2 | Add Inverter data point : Total apparent power |
| V1.1.14 | 2017-11-18 | Add Inverter model: SG15KTL-M, SG20KTL-M |
| V1.1.15 | 2017-11-25 | Add Inverter model: SG30KTL-M Add Inverter fault/alarm code: 116 |
| V1.1.16 | 2017-12-22 | Add Inverter model:SG111HV Modify SG10KTL-M, SG12KTL-M limit the maximum power ratio of 110% |

| V1.1.17 | 2018-1-18 | Increase the support of “Total apparent power” point inverter model information |
| --- | --- | --- |
| V1.1.18 | 2018-03-17 | Delete some product types according to overseas sales list. “U1 Limit” default value is adjusted to 950. Add Inverter fault/alarm code: 117 |
| V1.1.19 | 2018-04-24 | Add Inverter fault/alarm code: 34/106 Add country code: US-NE |
| V1.1.20 | 2018-05-24 | Add PID work state, PID night recovery, PID day protection, PID alarm code |
| V1.1.21 | 2018-06-15 | Adjust the description of fault code 44 Adjust the description of fault code23/40 Add Inverter fault/alarm code:45/46 Add Appendix 5 |
| V1.2.22 | 2018-08-07 | Add Inverter fault/alarm code:105 Add Inverter model : SG110HV-M |
| V1.1.23 | 2018-8-17 | Adjust the description of fault code2/15 |
| V1.1.24 | 2018-08-31 | Add Inverter data point : DC Voltage 6 –DC Voltage 12, DC current 6 –DC current 12; Current of 19thinput–Current of 24thinput Delete the fault/alarm code 6/26/75 Adjust the description of fault code 15/74 |
| V1.1.25 | 2018-09-18 | Adjust address :DC Voltage 9 –DC Voltage 12, DC current 9 –DC current 12 Add country code: MYS/PHL， Add Inverter fault/alarm code: 566/567/568/569/570/571,582/583/584/585/586/587 |
| V1.1.26 | 2018-11-7 | Add Inverter fault/alarm code:448-471 |
| V1.1.27 | 2018-11-7 | Add Inverter model: SG33CX, SG40CX, SG50CX, SG110CX, Add SG5-20K Meter information(read-only register:5083-0104, holding register:5009-5015 ) Modify the name of fault code: 030/031/032/033/042 Add Q(U)/Q(P) curve definition |
| V1.1.28 | 2019-4-9 | Add Inverter model: SG250HX |
| V1.1.29 | 2019-5-23 | Add Inverter fault/alarm code: 220/221/222/223/224/225/226/227/514 Modify the SG250HX power limitation setting range 0-1110, See Appendix 6. Add Inverter model: SG30CX/SG36CX-US/SG60CX-US/SG250HX-US |
| V1.1.30 | 2019-9-21 | Add Inverter model: SG25CX-SA/SG100CX-JP, SG250HX-IN |
| V1.1.31 | 2020-3-12 | Add Inverter fault code 1500-1531 |

| V1.1.32 | 2020-6-17 | Adjust the description and applicable Inverter of points, update Appendix6, Appendix 9, Appendix10 |
| --- | --- | --- |
| V1.1.33 | 2020-7-10 | Add Inverter model: SG250HX-IN-20 |
| V1.1.34 | 2020-8-15 | Add Full-Day PID Suppression, Installed PV Power |
| V1.1.35 | 2021-1-28 | - Add Inverter model:SG75CX - Update Country ID - Add 100% Scheduling to Achieve Active Overload |
| V1.1.36 | 2021-2-7 | - Add Inverter model: SG3.0RT, SG4.0RT, SG5.0RT, SG6.0RT, SG7.0RT,SG8.0RT, SG10RT, SG12RT, SG15RT, SG17RT, SG20RT |
| V1.1.37 | 2021-7-12 | - Add Inverter model: SG5.5RS-JP，SG49.5CX-JP - RT series machines do not support PID protection function, the model description in the protocol is deleted (measuring point 5042) |
| V1.1.38 | 2021-7-20 | - Add Inverter model: SG0.7RS-S, SG1.0RS-S, SG1.5RS-S, SG2.0RS-S, SG2.5RS-S, SG3.0RS-S SG3.0RS, SG3.6RS, SG4.0RS, SG5.0RS, SG6.0RS SG8.0RS, SG9.0RS, SG10RS, SG5.0RS-ADA - Modify the fault code description to be consistent with the product specification |
| V1.1.39 | 2021-10-18 | - Add Inverter model: SG320HX, SG350HX, SG125HX-JP |
| V1.1.40 | 2021-12-25 | - Add Inverter model: SG125CX-P2, SG25/30/33/36/40/50CX-P2 - Add Quick grid dispatch mode(32569) - Add Swift grid dispatch mode(32570) |
| V1.1.41 | 2022-4-2 | - Modify SG125CX-P2 - Modify 100% Scheduling to Achieve Active Overload to Active Power Overload |
| V1.1.42 | 2022-4-29 | - Add Protocol num、Protocol ver、Arm software ver、DSP software ver - Supplement series of SGRT - Modified Overload Rate of Belgium |
| V1.1.43 | 2022-5-26 | - Add String 15-24 current |
| V1.1.44 | 2022-6-13 | - Update model information of SG320HX/SG350HX |
| V1.1.45 | 2022-6-28 | - MPPT voltage and current extended to route 16, String current extended to route 32. - In Q(U) curve, the data type of QU_Q1, QU _Q2, QU _Q3 and QU _Q4 is changed to S16. - Add Inverter model: SG125HX. - Device fault code update. |
| V1.1.46 | 2022-7-21 | - Add Inverter model:SG110CX-P2 |

| V1.1.47 | 2022-9-16 | 1. Add Inverter model: 1）SG285HX 2）SG333HX |
| --- | --- | --- |
| V1.1.48 | 2022-09-24 | Modify the description of SGRT series |
| V1.1.49 | 2022-10-10 | 1. Add Inverter model:SG75CX-P2 |
| V1.1.50 | 2022-12-02 | - Add Heart Beat(5143) |
| V1.1.51 | 2022-12-30 | - Add Inverter model: SG350HX-US - Use SG225-350HX replace SG225HX，SG250HX， SG320HX，SG350HX … |
| V1.1.52 | 2023-01-03 | - Modify the model code of the following models： SG3.0/4.0/5.0/6.0/7.0/8.0/10/12/15/17/20/23/25RT-P2 |
| V1.1.53 | 2023-01-13 | - Device type code of SG350HX-US revised as 0x2C4F |

Valid for device types:

In production:

## SG5.5RS-JP, SG0.7RS-S, SG1.0RS-S, SG1.5RS-S, SG2.0RS-S, SG2.5RS-S, SG3.0RS-S, SG3.0RS, SG3.6RS, SG4.0RS, SG5.0RS, SG6.0RS, SG8.0RS, SG9.0RS, SG10RS, SG5.0RS-ADA

RT Series：

（1）SG3.0/4.0/5.0/6.0/7.0/8.0/10/12/15/17/20RT

（2）SG3.0/4.0/5.0/6.0/7.0/8.0/10/12/15/17/20RT-P2

SG225-350HX： SG225HX，SG250HX，SG320HX，SG350HX

SG30KTL-M, SG30KTL-M-V31, SG33KTL-M, SG36KTL-M, SG33K3J, SG49K5J, SG34KJ, LP_P34KSG, SG49.5CX-JP, SG50KTL-M-20, SG60KTL, G80KTL, SG80KTL-20, SG60KU-M

SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M

SG80KTL-M, SG85BF, SG80HV, SG80BF, SG110HV-M, SG111HV, SG125HV, SG125HV-20

SG25CX-SA, SG30CX, SG33CX, SG40CX, SG50CX, SG36CX-US, SG60CX-US, SG75CX, SG100CX SG100CX-JP, SG110CX, SG136TX, SG285HX，SG333HX、SG350HX-US

SG250HX-IN, SG250HX-US, SG125HX-JP, SG125HX

SG125CX-P2, SG25/30/33/36/40/50CX-P2, SG110CX-P2,SG75CX-P2

Discontinued:

## SG30KTL, SG10KTL, SG12KTL, SG15KTL, SG20KTL, SG30KU, SG36KTL, SG36KU, SG40KTL, SG40KTL-M, SG50KTL-M, SG60KTL-M, SG60KU

Statement:

All hardware versions of SG60KTL share one device type code.

# Introduction

This communication adopts modbus RTU protocol, and applies to the communication between Sungrow PV grid- connected string inverters and the upper computer (PC) monitoring software. This protocol can read the real-time operating data and fault states of inverters.

- Communication Interface

## RS485

|  | Default setting |
| --- | --- |
| Address | Inverter: 1 - 247 settable PC: 1 - 247 settable |
| Broadcast | Yes |
| Baud rate | 9600bit/s |
| Check bit | Null or settable |
| Data bit | 8 |
| Stop bit | 1 |
| Mode | RTU |
| Appliance interface | RS485-2W cable connection |

  - Ethernet (optional) Default:

## -	IP: 192.168.1.100;

-	Sub-Net: 255.255.0.0

-	Port: 502

# Definition of Address

- Data type

U16: 16-bit unsigned integer, big-endian S16: 16-bit signed integer, big-endian

U32: 32-bit unsigned integer; little-endian for double-word data. Big-endian for byte data S32: 32-bit signed integer; little-endian for double-word data. Big-endian for byte data Example:

transmission order of U16 data 0x0102 is 01, 02 transmission order of U32 data 0x01020304 is 03, 04, 01, 02

The transmission order of multibyte data UTF-8: the high-byte data is in the front and the low-byte data is at back. Example: transmission order of UTF-8 data ABCD is A, B, C, D.

- Value description

The decimal parameters are transmitted as integer after expansion. For example: 10.333 KW is transmitted as 10333;

800.5 V is transmitted as 8005. Negative numbers are transmitted as complement, 0xFFFF signifying -1. Unavailable register cannot be viewed or set. The return of unsigned number is F, For example: “0xFFFF” is the return for U16, “0xFFFFFFFF” is the return for U32; the return of signed number is the max. positive number, e.g. “0x7FFF” for S16, “0x7FFFFFFF” for S32; 0x00 for UTF-8. UTF-8 occupies 1 byte. The length of odd number is complemented by 0x00.

Example:

SG80KTL only one MPPT input,

MPPT 2 voltage (5013)

MPPT 2 current (5014)

MPPT 3 voltage (5015)

MPPT 3 current (5016)

MPPT 4 voltage (5115)

MPPT 4 current (5116), The data for these registers are 0xFFFF.

- Address type

Address of 3x type is read-only register, supporting the CMD code inquiry of 0x04.

Address of 4x type is holding register, supporting the CMD code inquiry of 0x03, and CMD codes write-in of 0x10 and 0x06. CMD codes 0x10 and 0x06 support the broadcast address.

Support Modbus error code 02 (address error), 04 (setting failure).

Visit all registers by subtracting 1 from the register address. Example: if the address is 5000 –5001, visit it using address 4999 –5000. Entering “01 04 1387 00 02 + CRC” to check the data of address 5000 –5001.

- Verify type

CRC16 generates polynomial 0xA001, little-endian.

3.1	Running information variable address definition (read-only register, Address type: 3X)

| No. | Name | Address | Data type | Data range | Unit | Note |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Protocol num | 4950 - 4951 | U32 |  |  |  |
| 2. | Protocol ver | 4952 - 4953 | U32 |  |  |  |
| 3. | Arm software ver | 4954 - 4968 | U16 |  |  |  |
| 4. | DSP software ver | 4969 - 4983 | U16 |  |  |  |
| 5. | Reserved | 4984 - 4989 | U16 |  |  |  |
| 6. | SN | 4990 - 4999 | UTF-8 |  |  | Data type :UTF-8 |
| 7. | Device type code | 5000 | U16 |  |  | See Appendix 5 |
| 8. | Nominal active power | 5001 | U16 |  | 0.1kW |  |

| 9. | Output type | 5002 | U16 | 0-two phase; 1-3P4L; 2-3P3L |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 10. | Daily power yields | 5003 | U16 |  | 0.1 kWh |  |
| 11. | Total power yields | 5004 - 5005 | U32 |  | kWh |  |
| 12. | Total running time | 5006 - 5007 | U32 |  | h |  |
| 13. | Internal temperature | 5008 | S16 |  | 0.1℃ |  |
| 14. | Total apparent power | 5009 - 5010 | U32 |  | VA | Valid for inverters: SG5KTL-MT SG6KTL-MT SG8KTL-M SG10KTL-M SG10KTL-MT SG12KTL-M SG15KTL-M SG17KTL-M SG20KTL-M RT Series SG33K3J SG36KTL-M SG40KTL-M SG50KTL SG50KTL-M SG60KTL SG60KTL-M SG60KU-M SG80KTL SG80KTL-M SG111HV SG125HV SG125HV-20 SG33CX SG40CX SG50CX SG110CX |

|  |  |  |  |  |  | SG30CX SG36CX-US SG60CX-US SG49.5CX-JP SG25CX-SA SG100CX SG75CX SG225-350HX SG125CX-P2 SG110CX-P2 SG75CX- P2SG25/30/33/36/40/50CX-P2 |
| --- | --- | --- | --- | --- | --- | --- |
| 15. | MPPT 1 voltage | 5011 | U16 |  | 0.1V | See Appendix 5 |
| 16. | MPPT 1 current | 5012 | U16 |  | 0.1A |  |
| 17. | MPPT 2 voltage | 5013 | U16 |  | 0.1V |  |
| 18. | MPPT 2 current | 5014 | U16 |  | 0.1A |  |
| 19. | MPPT 3 voltage | 5015 | U16 |  | 0.1V |  |
| 20. | MPPT 3 current | 5016 | U16 |  | 0.1A |  |
| 21. | Total DC power | 5017 - 5018 | U32 |  | W |  |
| 22. | A-B line voltage/phase A voltage | 5019 | U16 |  | 0.1 V | Output type (address: 5002) is 1: upload phase voltage; 2: upload line voltage Except SG5.5RS-JP |
| 23. | B-C line Voltage/phase B Voltage | 5020 | U16 |  | 0.1 V | Output type (address: 5002) is 1: upload phase voltage; 2: upload line voltage Except SG5.5RS-JP |
| 24. | C-A line Voltage/phase C Voltage | 5021 | U16 |  | 0.1 V | Output type (address: 5002) is 1: upload phase voltage; 2: upload line voltage Except SG5.5RS-JP |
| 25. | Phase A current | 5022 | U16 |  | 0.1 A | Except SG5.5RS-JP |
| 26. | Phase B current | 5023 | U16 |  | 0.1 A | Except SG5.5RS-JP |
| 27. | Phase C current | 5024 | U16 |  | 0.1 A | Except SG5.5RS-JP |

| 28. | Reserved | 5025 - 5026 | U32 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 29. | Reserved | 5027 - 5028 | U32 |  |  |  |
| 30. | Reserved | 5029 - 5030 | U32 |  |  |  |
| 31. | Total active power | 5031 - 5032 | U32 |  | W |  |
| 32. | Total reactive power | 5033–5034 | S32 |  | Var |  |
| 33. | Power factor | 5035 | S16 |  | 0.001 | >0 means leading <0 means lagging |
| 34. | Grid frequency | 5036 | U16 |  | 0.1 Hz |  |
| 35. | Reserved | 5037 | U16 |  |  |  |
| 36. | Work state | 5038 | U16 | See Appendix 1 |  | Data of address 5039 - 5045 are additional |
|  | Fault/Alarm time: Year | 5039 | U16 |  |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100). Except SG5.5RS-JP , SG0.7/1.0/1/5/2.0/2.5/3.0RS-S, SG3.0/3.6/4.0/5.0/6.0RS, SG5.0RS-ADA, SG8.0/9.0/10RS |
|  | Fault/Alarm time: Month | 5040 | U16 |  |  |  |
|  | Fault/Alarm time: Day | 5041 | U16 |  |  |  |
|  | Fault/Alarm time: Hour | 5042 | U16 |  |  |  |
|  | Fault/Alarm time: Minute | 5043 | U16 |  |  |  |
|  | Fault/Alarm time: Second | 5044 | U16 |  |  |  |
|  | Fault/Alarm code 1 | 5045 | U16 | See Appendix 3 |  |  |
|  | Reserved | 5046 - 5048 | U16 |  |  |  |
| 37. | Nominal reactive power | 5049 | U16 |  | 0.1kVar |  |
| 38. | Reserved | 5050 - 5070 | U32 |  |  |  |
| 39. | Array insulation resistance | 5071 | U16 | 1 - 20000(0xFFFF: invalid) | 1kΩ |  |
| 40. | Reserved | 5072 | U16 |  |  |  |
| 41. | Reserved | 5073-5076 |  |  |  |  |
| 42. | Active Power | 5077 - | U32 |  | 1w | Except SG5.5RS-JP |

|  | Regulation Setpoint | 5078 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 43. | Reactive Power Regulation Setpoint | 5079-5080 | S32 |  | 1Var |  |
| 44. | Work state | 5081 - 5082 | U32 |  |  | See Appendix 2 Except SG5.5RS-JP |
| 45. | Meter power | 5083~5084 | S32 |  | 1w | Valid for inverters: SG5KTL-MT SG6KTL-MT SG8KTL-M SG10KTL-M SG10KTL-MT SG12KTL-M SG15KTL-M SG17KTL-M SG20KTL-M Note: Country set to Europe Area. |
| 46. | Meter A phase power | 5085~5086 | S32 |  | 1w |  |
| 47. | Meter B phase power | 5087~5088 | S32 |  | 1w |  |
| 48. | Meter C phase power | 5089~5090 | S32 |  | 1w |  |
| 49. | Load power | 5091~5092 | S32 |  | 1w |  |
| 50. | Daily export energy | 5093~5094 | U32 |  | 0.1kWh |  |
| 51. | Total export energy | 5095~5096 | U32 |  | 0.1kWh |  |
| 52. | Daily import energy | 5097~5098 | U32 |  | 0.1kWh |  |
| 53. | Total import energy | 5099~5100 | U32 |  | 0.1kWh |  |
| 54. | Daily direct energy consumption | 5101~5102 | U32 |  | 0.1kWh |  |
| 55. | Total direct energy consumption | 5103~5104 | U32 |  | 0.1kWh |  |
| 56. | Reserved | 5105 - 5112 |  |  |  |  |
| 57. | Daily running time | 5113 | U16 |  | 1min |  |
| 58. | Present country | 5114 | U16 |  |  |  |
| 59. | MPPT 4 voltage | 5115 | U16 |  | 0.1V | See Appendix 5 Except SG5.5RS-JP |
| 60. | MPPT 4 current | 5116 | U16 |  | 0.1A |  |
| 61. | MPPT 5 voltage | 5117 | U16 |  | 0.1V |  |
| 62. | MPPT 5 current | 5118 | U16 |  | 0.1A |  |

| 63. | MPPT 6 voltage | 5119 | U16 |  | 0.1V |  |
| --- | --- | --- | --- | --- | --- | --- |
| 64. | MPPT 6 current | 5120 | U16 |  | 0.1A |  |
| 65. | MPPT 7 voltage | 5121 | U16 |  | 0.1V |  |
| 66. | MPPT 7 current | 5122 | U16 |  | 0.1A |  |
| 67. | MPPT 8 voltage | 5123 | U16 |  | 0.1V |  |
| 68. | MPPT 8 current | 5124 | U16 |  | 0.1A |  |
| 69. | Reserved | 5125 |  |  |  |  |
| 70. | Reserved | 5126 - 5127 |  |  |  |  |
| 71. | Monthly power yields | 5128 - 5129 | U32 |  | 0.1kWh |  |
| 72. | MPPT 9 voltage | 5130 | U16 |  | 0.1V | See Appendix 5 Except SG5.5RS-JP |
| 73. | MPPT 9 current | 5131 | U16 |  | 0.1A |  |
| 74. | MPPT 10 voltage | 5132 | U16 |  | 0.1V |  |
| 75. | MPPT 10 current | 5133 | U16 |  | 0.1A |  |
| 76. | MPPT 11 voltage | 5134 | U16 |  | 0.1V |  |
| 77. | MPPT 11 current | 5135 | U16 |  | 0.1A |  |
| 78. | MPPT 12 voltage | 5136 | U16 |  | 0.1V |  |
| 79. | MPPT 12 current | 5137 | U16 |  | 0.1A |  |
| 80. | Reserved | 5138 - 5139 | U16 |  |  |  |
| 81. | Work status1 | 5140 | U16 | - : standby - : running - : Derating - : quota - : scheduled outage - : limit outage - : error outage |  | Xinjiang power grid requirements Valid for inverters: SG5-25KTL_M SG125HV SG33-50CX SG100-136TX SG80—110HV-M SG225-350HX SG85BF |

|  |  |  |  |  |  | SG80KTL-M RT Series |
| --- | --- | --- | --- | --- | --- | --- |
| 82. | Work status2 | 5141 | U16 | - : running - : shut down - : overhaul - : standby |  | Valid for inverters: SG5-25KTL_M SG125HV SG33-50CX SG100-136TX SG80—110HV-M SG225-350HX SG85BF SG80KTL-M RT Series |
| 83. | Reserved | 5142 |  |  |  |  |
| 84. | Heart Beat | 5143 | U16 |  |  |  |
| 85. | Total power yields | 5144 - 5145 | U32 |  | 0.1kWh | (Display accuracy increased to 0.1kWh) Valid for inverters: SG5KTL-MT SG6KTL-MT SG8KTL-M SG10KTL-M SG10KTL-MT SG12KTL-M SG15KTL-M SG17KTL-M SG20KTL-M RT Series SG80KTL-M SG111HV SG125HV SG125HV-20 SG33CX SG40CX SG50CX SG110CX SG30CX SG36CX-US SG60CX-US SG49.5CX-JP SG25CX-SA SG100CX SG75CX SG225-350HX SG125CX-P2 SG110CX-P2 |

|  |  |  |  |  |  | SG75CX-P2 SG25/30/33/36/40/50CX-P2 |
| --- | --- | --- | --- | --- | --- | --- |
| 86. | Negative voltage to the ground | 5146 | S16 | -15000~15000 | 0.1V | Except SG5.5RS-JP |
| 87. | Bus voltage | 5147 | U16 | 0 - 15000 | 0.1V |  |
| 88. | Grid frequency | 5148 | U16 |  | 0.01Hz | (Display accuracy increased to 0.01Hz) Valid for inverters: SG5KTL-MT SG6KTL-MT SG8KTL-M SG10KTL-M SG10KTL-MT SG12KTL-M SG15KTL-M SG17KTL-M SG20KTL-M RT Series SG80KTL-M SG111HV SG125HV SG125HV-20 SG33CX SG40CX SG50CX SG110CX SG30CX SG36CX-US SG60CX-US SG49.5CX-JP SG25CX-SA SG100CX SG75CX SG225-320HX SG125CX-P2 SG110CX-P2 SG75CX-P2 SG25/30/33/36/40/50CX-P2 |
| 89. | Reserved | 5149 | U16 | 0~15000 | 0.1V |  |
| 90. | PID work state | 5150 | U16 | 2: PID Recover Operation 4: Anti-PID Operation 8: PID Abnormity |  | Valid for inverters: SG5KTL-MT SG6KTL-MT SG8KTL-M SG10KTL-M |

|  |  |  |  |  |  | SG10KTL-MT SG12KTL-M SG15KTL-M SG17KTL-M SG20KTL-M RT Series SG80KTL-M SG125HV SG125HV-20 SG80KTL SG30CX SG33CX SG40CX SG50CX SG110CX SG100CX SG75CX SG136TX SG36CX-US SG60CX-US SG49.5CX-JP SG25CX-SA SG225-320HX SG125CX-P2 SG110CX-P2 SG75CX-P2 SG25/30/33/36/40/50CX-P2 SG0.7RS-S SG1.0RS-S SG1.5RS-S SG2.0RS-S SG2.5RS-S SG3.0RS-S SG3.0RS SG3.6RS SG4.0RS SG5.0RS SG6.0RS SG8.0RS SG9.0RS SG10RS SG5.0RS-ADA |
| --- | --- | --- | --- | --- | --- | --- |
| 91. | PID alarm code | 5151 | U16 | 432:PID resistance abnormal 433:PID function |  | See Appendix 4 |

|  |  |  |  | abnormal 434:PID overvoltage/overcurrent protection |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 92. | Reserved | 5152-5185 | U16 |  |  |  |
| 93. | MPPT 13 voltage | 5186 | U16 |  | 0.1V |  |
| 94. | MPPT 13 current | 5187 | U16 |  | 0.1A |  |
| 95. | MPPT 14 voltage | 5188 | U16 |  | 0.1V |  |
| 96. | MPPT 14 current | 5189 | U16 |  | 0.1A |  |
| 97. | MPPT 15 voltage | 5190 | U16 |  | 0.1V |  |
| 98. | MPPT 16 current | 5191 | U16 |  | 0.1A |  |
| 99. | MPPT 16 voltage | 5192 | U16 |  | 0.1V |  |
| 100. | MPPT 16 current | 5193 | U16 |  | 0.1A |  |
| 101. | Reserved | 5194-7012 |  |  |  |  |
| 1. | String 1 current | 7013 | U16 |  | 0.01A | Before checking the current information of one input, please make sure the hardware supports this function. If parameter can be viewed in the LCD panel or APP software(default menu-running information), the corresponding address is readable. Number of strings, please see Appendix 5 Except SG5.5RS-JP |
| 2. | String 2 current | 7014 | U16 |  | 0.01A |  |
| 3. | String 3 current | 7015 | U16 |  | 0.01A |  |
| 4. | String 4 current | 7016 | U16 |  | 0.01A |  |
| 5. | String 5 current | 7017 | U16 |  | 0.01A |  |
| 6. | String 6 current | 7018 | U16 |  | 0.01A |  |
| 7. | String 7 current | 7019 | U16 |  | 0.01A |  |
| 8. | String 8 current | 7020 | U16 |  | 0.01A |  |
| 9. | String 9 current | 7021 | U16 |  | 0.01A |  |
| 10. | String 10 current | 7022 | U16 |  | 0.01A |  |

| 11. | String 11 current | 7023 | U16 |  | 0.01A |  |
| --- | --- | --- | --- | --- | --- | --- |
| 12. | String 12 current | 7024 | U16 |  | 0.01A |  |
| 13. | String 13 current | 7025 | U16 |  | 0.01A |  |
| 14. | String 14 current | 7026 | U16 |  | 0.01A |  |
| 15. | String 15 current | 7027 | U16 |  | 0.01A |  |
| 16. | String 16 current | 7028 | U16 |  | 0.01A |  |
| 17. | String 17 current | 7029 | U16 |  | 0.01A |  |
| 18. | String 18 current | 7030 | U16 |  | 0.01A |  |
| 19. | String 19 current | 7031 | U16 |  | 0.01A |  |
| 20. | String 20 current | 7032 | U16 |  | 0.01A |  |
| 21. | String 21 current | 7033 | U16 |  | 0.01A |  |
| 22. | String 22 current | 7034 | U16 |  | 0.01A |  |
| 23. | String 23 current | 7035 | U16 |  | 0.01A |  |
| 24. | String 24 current | 7036 | U16 |  | 0.01A |  |
| 25. | String 25 current | 7037 | U16 |  | 0.01A |  |
| 26. | String 26 current | 7038 | U16 |  | 0.01A |  |
| 27. | String 27 current | 7039 | U16 |  | 0.01A |  |
| 28. | String 28 current | 7040 | U16 |  | 0.01A |  |
| 29. | String 29 current | 7041 | U16 |  | 0.01A |  |
| 30. | String 30 current | 7042 | U16 |  | 0.01A |  |
| 31. | String 31 current | 7043 | U16 |  | 0.01A |  |
| 32. | String 32 current | 7044 | U16 |  | 0.01A |  |

a)	Parameter setting address definition (holding register, Address type: 4X)

| No. | Name |  | Address | Data type | Data range | Unit | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | System clock: Year |  | 5000 | U16 |  |  | Receive time synchronization setting of the monitoring system |
| 2 | System clock: Month |  | 5001 | U16 |  |  |  |
| 3 | System clock: Day |  | 5002 | U16 |  |  |  |
| 4 | System clock: Hour |  | 5003 | U16 |  |  |  |
| 5 | System clock: Minute |  | 5004 | U16 |  |  |  |
| 6 | System clock: Second |  | 5005 | U16 |  |  |  |
| 7 | Start/Stop |  | 5006 | U16 | 0xCF (Start) 0xCE (Stop) |  |  |
| 8 | Power limitation switch |  | 5007 | U16 | 0xAA: Enable; 0x55: Disable |  |  |
| 9 | Power limitation setting |  | 5008 | U16 | See Appendix 5 | 0.1% | Available when the power limitation switch (5007) is enabled |
| 10 | Reserved |  | 5009 | U16 |  |  | Valid for inverters: SG5KTL-MT SG6KTL-MT SG8KTL-M SG10KTL-M SG10KTL-MT SG12KTL-M SG15KTL-M SG17KTL-M SG20KTL-M Note: Country set to Europe Area. Except SG0.7/1.0/1/5/2.0/2.5/3.0RS- S, SG3.0/3.6/4.0/5.0/6.0RS, SG5.0RS-ADA, SG8.0/9.0/10RS whose address is 5012 - 5014 |
| 11 | Export power limitation |  | 5010 | U16 | 0xAA: Enable; 0x55: Disable |  |  |
| 12 | Export power limitation value |  | 5011 | U16 | 0-Rated active power |  |  |
| 13 | Current transformer output current |  | 5012 | U16 | 1-100 | A |  |
| 14 | Current transformer range |  | 5013 | U16 | 1-10000 | A |  |
| 15 | Current transformer |  | 5014 | U16 | 0- Internal 1- External |  |  |
| 16 | Export power limitation percentage |  | 5015 | U16 | 0~1000 | 0.1% |  |
| 17 | Installed PV Power |  | 5016 | U16 | 0-30000 | 0.01KW |  |

| 18 | Power factor setting | 5019 | S16 | -1000 - -800 800 - 1000 | 0.001 | Available when the reactive power adjustment switch (5036) is set to power factor setting valid (0xA1) > 0 means leading < 0 means lagging |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Valid for inverters: |
|  |  |  |  |  |  | SG33CX |
|  |  |  |  |  |  | SG40CX |
|  |  |  |  |  |  | SG50CX |
|  |  |  |  |  |  | SG75CX |
|  |  |  |  |  |  | SG110CX |
|  |  |  |  |  |  | SG136TX |
|  |  |  |  |  |  | SG30CX |
|  |  |  |  |  |  | SG36CX-US |
|  |  |  |  |  |  | SG60CX-US |
|  |  |  |  |  |  | SG49.5CX-JP |
| 19 | Active Power Overload | 5020 | U16 | 0xAA: Enable; 0x55: Disable |  | SG225-350HX SG25/30/33/36/40/50CX-P2 SG25CX-SA |
|  |  |  |  |  |  | SG100CX RT Series NOTE:When Active Power Overload |
|  |  |  |  |  |  | is disabled: inverters will generate |
|  |  |  |  |  |  | power according to the command |
|  |  |  |  |  |  | value. |
|  |  |  |  |  |  | When Active Power Overload is |
|  |  |  |  |  |  | enabled: inverters will generate |
|  |  |  |  |  |  | power according to the product of the |
|  |  |  |  |  |  | command value and the overload |
|  |  |  |  |  |  | rate. |
| 20 | Local / remote control | 5021 - 5033 | U16 | - : unvalid - : valid |  |  |
|  |  |  |  |  |  | Valid for inverters: |
|  |  |  |  |  |  | RT Series |
|  |  |  |  |  |  | SG80KTL-M |
|  |  |  |  |  |  | SG125HV-20 |
| 21 | Night SVG Switch | 5035 | U16 | 0xAA: Enable; 0x55: Disable |  | SG33CX SG40CX SG50CX |
|  |  |  |  |  |  | SG110CX |
|  |  |  |  |  |  | SG136TX |
|  |  |  |  |  |  | SG225-350HX |
|  |  |  |  |  |  | SG125CX-P2 |

|  |  |  |  |  |  | SG110CX-P2 SG75CX-P2 SG25/30/33/36/40/50CX-P2 SG30CX SG36CX-US SG60CX-US SG49.5CX-JP SG25CX-SA SG100CX SG75CX |
| --- | --- | --- | --- | --- | --- | --- |
| 22 | Reactive power adjustment mode | 5036 | U16 | 0x55: OFF, power factor returns to 1, reactive power percentage returns to 0; 0xA1: power factor setting valid, Reactive power percentage returns to 0; 0xA2: Reactive power percentage setting valid, power factor returns to 1; 0xA3: Enable Q(P) curve configuration; 0xA4: Enable Q(U) curve configuration |  | The SG5.5RS-JP doesn’t support 0xA2, 0xA3, 0xA4 |
| 23 | Reactive power percentage setting | 5037 | S16 | 0 - 1000 0 - -1000 | 0.1% | Available when the reactive power adjustment switch (5036) is set to Reactive power percentage setting valid (0xA2) |
| 24 | Reserved | 5038 |  |  |  |  |
| 25 | Power limitation adjustment | 5039 | U16 | See Appendix 5 | 0.1kW | Available when the power limitation switch (5007) is enabled Except SG5.5RS-JP |
| 26 | Reactive power adjustment | 5040 | S16 | See Appendix 5 | 0.1kVar | Available when the reactive power adjustment switch (5036) is set to Reactive power percentage setting valid (0xA2) Except SG0.7/1.0/1/5/2.0/2.5/3.0RS- |

|  |  |  |  |  |  | S, SG3.0/3.6/4.0/5.0/6.0RS, SG5.0RS-ADA, SG8.0/9.0/10RS |
| --- | --- | --- | --- | --- | --- | --- |
| 27 | PID Recovery | 5041 | U16 | 0xAA: Enable; 0x55: Disable |  | Valid for inverters: SG5KTL-MT (EU exclueded) SG6KTL-MT (EU exclueded) SG8KTL-M (EU exclueded) SG10KTL-M (EU exclueded) SG10KTL-MT (EU exclueded) SG12KTL-M (EU exclueded) SG15KTL-M (EU exclueded) SG17KTL-M (EU exclueded) SG20KTL-M (EU exclueded) RT Series SG80KTL-M SG125HV SG125HV-20 SG80KTL SG33CX SG40CX SG50CX SG100CX SG75CX SG110CX SG136TX SG225-350HX SG30CX SG36CX-US SG60CX-US SG49.5CX-JP SG25CX-SA SG125CX-P2 SG110CX-P2 SG75CX-P2 SG25/30/33/36/40/50CX-P2 |
| 28 | Anti-PID | 5042 | U16 | 0xAA: Enable; 0x55: Disable |  | Valid for inverters: SG125HV SG125HV-20 SG225-350HX SG136TX/SG100CX-JPExcept SG0.7/1.0/1/5/2.0/2.5/3.0RS-S, SG3.0/3.6/4.0/5.0/6.0RS, SG5.0RS- ADA, SG8.0/9.0/10RS |
| 29 | Full-Day PID | 5043 | U16 | 0xAA: Enable; |  | Valid for inverters: |

|  | Suppression |  |  | 0x55: Disable |  | HX Except SG0.7/1.0/1/5/2.0/2.5/3.0RS- S, SG3.0/3.6/4.0/5.0/6.0RS, SG5.0RS-ADA, SG8.0/9.0/10RS |
| --- | --- | --- | --- | --- | --- | --- |
| 30 | Reserved | 5043 - 5047 |  |  |  |  |
| 31 | Q(P) curve 1 | 5048-5077 |  | See Appendix 6 Note: The reactive power adjustment switch (5036) is set to Enable Q(P) curve (0xA3) |  | Except inverters :CX/HX/TX |
| 32 | Q(U) curve 1 | 5078-5115 |  | See Appendix 7 Note: The reactive power adjustment switch (5036) is set to Enable Q(U) curve (0xA4) |  | Except inverters :CX/HX/TX |
| 33 | Q(P) curve 2 | 5116-5134 |  | See Appendix 8 Note: The reactive power adjustment switch (5036) is set to Enable Q(P) curve (0xA3) |  | Valid for inverters: RT Series SG33CX/SG40CX/SG50CX/ SG110CX/ SG30CX/SG36CX-US/ SG60CX-US/SG49.5CX-JP / SG225-350HX / SG25CX-SA SG100CX/SG75CX |
| 34 | Q(U) curve 2 | 5135-5154 |  | See Appendix 9 Note: The reactive power adjustment switch (5036) is set to Enable Q(U) curve (0xA4) |  | Valid for inverters: SG33CX/SG40CX/SG50CX/ SG110CX / SG30CX//SG36CX-US/ SG60CX-US/ SG49.5CX-JP / SG225-350HX / SG25CX-SA SG100CX/SG75CX RT Series |
| 35 | Reserved | 5155-5199 |  |  |  |  |
| 36 | Quick grid dispatch mode | 32569 | U16 | 0xAA: Enable; 0x55: Disable |  | Valid for inverters: SG320HX SG350HX SG285HX SG333HX SG350HX-US |
| 37 | Swift grid dispatch mode | 32570 | U16 | 0xAA: Enable; 0x55: Disable |  | Valid for inverters: SG320HX |

|  |  |  |  |  |  | SG350HX SG285HX SG333HX SG350HX-US |
| --- | --- | --- | --- | --- | --- | --- |

Appendix

Appendix 1 Device Work State 1

| Device state (register 5038) |  |  |  |
| --- | --- | --- | --- |
| State | Value read by register 5038 | Paraphrase | Grid-connected power generation |
| Run | 0x0 | After being energized, inverter tracks the PV arrays’ maximum power point (MPP) and converts the DC power into AC power. This is the normal operation mode | Yes |
| Stop | 0x8000 | Inverter is stopped. | No |
| Key stop | 0x1300 | Inverter will stop operation by manually “stop” via app. In this way, inverter internal DSP stops. To restart the inverter, manually start via app | No |
| Emergency Stop | 0x1500 |  | No |
| Standby | 0x1400 | Inverter enters standby mode when DC side input is insufficient. In this mode inverter will wait within the standby duration. | No |
| Initial standby | 0x1200 | The inverter is in the initial power-on standby state. | No |
| Starting | 0x1600 | The inverter is initializing and synchronizing with the grid | No |
| Alarm run | 0x9100 | Warning information is detected. | Yes |
| Derating run | 0x8100 | The inverter derates actively due to environmental factors such as temperature or altitude | Yes |
| Dispatch run | 0x8200 | The inverter runs according to the scheduling instructions received from the monitoring background | Yes |
| Fault | 0x5500 | If a fault occurs, inverter will automatically stop operation, and disconnect the AC relay. The fault information will be displayed in the app. Once the fault is removed in recovery time, inverter will automatically resume running. | No |
| Communicate fault | 0x2500 |  | Unconfirmed |
| Uninitialized | 0x1111 |  | No |

Appendix 2 Device Work State2

| Work State (5081 - 5082) |  | Note |
| --- | --- | --- |
| State | Corresponding BIT in address 5081- 5082 |  |
| Run | 0 | Total run state bit BIT17 |
| Stop | 1 | 1 |

| Key stop | 3 | 3 |
| --- | --- | --- |
| Emergency Stop | 5 | 5 |
| Standby | 4 | 4 |
| Initial standby | 2 | 2 |
| Starting | 6 | 6 |
| Alarm run | 10 | Total run state bit BIT17 |
| Derating run | 11 | Total run state bit BIT17 |
| Dispatch run | 12 | Total run state bit BIT17 |
| Fault | 9 | Total fault state bit BIT18 |
| Communicate fault | 13 | Total fault state bit BIT18 |
| Total run bit (device is grid- connected running) | 17 |  |
| Total fault bit (device is in fault stop state) | 18 |  |

Appendix 3 Device Fault Code（Note: Please refer to the product user manual for handling measures)

| Fault code | Fault name |
| --- | --- |
| 2, 3, 14, 15 | Grid Overvoltage |
| 4, 5 | Grid Undervoltage |
| 8 | Grid Overfrequency |
| 9 | Grid Underfrequency |
| 10 | Grid Power Outage |
| 12 | Excess Leakage Current |
| 13 | Grid Abnormal |
| 17 | Grid Voltage Imbalance |
| 28, 29, 208, 448-479 | PV Reserve Connection Fault |
| 532-547, 564-579 | PV Reverse Connection Alarm |
| 548-563, 580-595 | PV Abnormal Alarm |
| 37 | Excessively High Ambient Temperature |
| 43 | Excessively Low Ambient Temperature |
| 39 | Low System Insulation Resistance |
| 106 | Grounding Cable Fault |
| 88 | Electric Arc Fault |
| 84 | Reverse Connection Alarm of the Meter/CT |
| 514 | Meter Communication Abnormal Alarm |
| 323 | Grid Confrontation |
| 75 | Inverter Parallel Communication Alarm |
| 7, 11, 16, 19–25, 30–34, 36, 38, 40–42, 44–50, 52–58, 60–68, 85, 87, 92, 93, 100–105, 107–114, 116–124, 200–211, 248–255, 300–322, 324–326, 401–412, | System Fault |

| 600–603, 605, 608, 612, 616, 620, 622–624, 800, 802, 804, 807, 1096–1122 |  |
| --- | --- |
| 59, 70–72, 74, 76, 82, 83, 89, 77– 81, 216– 218, 220– 231, 432– 434, 500– 513, 515– 518, 900, 901, 910, 911 635,636,637,638 | System Alarm |
| 264-283 | MPPT Reverse Connection |
| 332-363 | Boost Capacitor Overvoltage Alarm |
| 364-395 | Boost Capacitor Overvoltage Fault |
| 1548-1579 | String Current Reflux |
| 1600-1611 | PV Grounding Fault |
| 1616 | System Hardware Fault |

Appendix 4 PID alarm code

| LCD or APP display (decimal) | Communication send data (hexadecimal) | Description | Note |
| --- | --- | --- | --- |
| 432 | 0x01B0 | PID impedance abnormity | - Check to ensure that the inverter is equipped with the PID regulation function. - Check whether the ISO impedance protection value is excessively high through the LCD or the APP, so as to ensure the requirements are met. - Check whether the positive and negative insulation resistances to earth of the battery panel are excessively low. - Please contact SUNGROW if the fault still exists. |
| 433 | 0x01B1 | PID function abnormity | - Check to ensure that the inverter is equipped with the PID regulation function. - Check device operating environment and ensure the transformer-side phase line or N line impedance to ground is normal. - Please contact SUNGROW if the fault still exists. |
| 434 | 0x01B2 | PID overvoltage/overcurrent protection | - Check if the actual ISO impedance is excessively large (greater than 1.5M ohms). - Check whether the set PID control duty cycle is excessively large. - Please contact SUNGROW if the fault still exists. |

Appendix 5 Device Information(Note: If the value of string/MPPT is 1, it indicates that no string information (7013-7036) is uploaded to the read-only memory.)

| Model | Type code | MPPT | String/MPPT | Power limited range(0.1%) | Power limited range (0.1kW) | Reactive power limited range(0.1kvar) |
| --- | --- | --- | --- | --- | --- | --- |
| SG30KTL | 0x27 | 2 | 4 | 0-1100 | 0-330 | -150-150 |
| SG10KTL | 0x26 | 2 | 3 | 0-1100 | 0-110 | -50-50 |
| SG12KTL | 0x29 | 2 | 3 | 0-1100 | 0-132 | -60-60 |
| SG15KTL | 0x28 | 2 | 3 | 0-1100 | 0-165 | -75-75 |
| SG20KTL | 0x2A | 2 | 3 | 0-1100 | 0-220 | -100-100 |
| SG30KU | 0x2C | 2 | 5 | 0-1100 | 0-330 | -150-150 |
| SG36KTL | 0x2D | 2 | 5 | 0-1100 | 0-396 | -180-180 |
| SG36KU | 0x2E | 2 | 5 | 0-1100 | 0-396 | -180-180 |
| SG40KTL | 0x2F | 2 | 4 | 0-1100 | 0-396 | -180-180 |
| SG40KTL-M | 0x0135 | 3 | 3 | 0-1100 | 0-440 | -200-200 |
| SG50KTL-M | 0x011B | 4 | 3 | 0-1100 | 0-550 | -250-250 |
| SG60KTL-M | 0x0131 | 4 | 4 | 0-1100 | 0-660 | -300-300 |
| SG60KU | 0x0136 | 1 | 8 | 0-1100 | 0-660 | -300-300 |
| SG30KTL-M | 0x0141 | 3 | 3;3;2 | 0-1000 | 0-300 | -150-150 |
| SG30KTL-M-V31 | 0x70 | 3 | 3;3;2 | 0-1000 | 0-300 | -150-150 |
| SG33KTL-M | 0x0134 | 3 | 3;3;2 | 0-1100 | 0-363 | -165-165 |
| SG36KTL-M | 0x74 | 3 | 3;3;2 | 0-1000 | 0-360 | -180-180 |
| SG33K3J | 0x013D | 3 | 3 | 0-1000 | 0-333 | -166-166 |
| SG49K5J | 0x0137 | 4 | 3 | 0-1000 | 0-495 | -247-247 |
| SG34KJ | 0x72 | 2 | 4 | 0-1000 | 0-340 | -170-170 |
| LP_P34KSG | 0x73 | 1 | 4 | 0-1000 | 0-340 | -170-170 |
| SG50KTL-M-20 | 0x011B | 4 | 3 | 0-1100 | 0-550 | -250-250 |
| SG60KTL | 0x010F | 1 | 14 | 0-1100 | 0-660 | -300-300 |
| SG80KTL | 0x0138 | 1 | 18 | 0-1000 | 0-800 | -400-400 |
| SG80KTL-20 | 0x0138 | 1 | 18 | 0-1000 | 0-800 | -400-400 |
| SG60KU-M | 0x0132 | 4 | 4 | 0-1100 | 0-660 | -300-300 |
| SG5KTL-MT | 0x0147 | 2 | 1 | 0-1100 | 0-55 | -25-25 |
| SG6KTL-MT | 0x0148 | 2 | 1 | 0-1100 | 0-66 | -30-30 |
| SG8KTL-M | 0x013F | 2 | 1 | 0-1100 | 0-88 | -40-40 |
| SG10KTL-M | 0x013E | 2 | 1 | Default: 0- 1100 If country is Germany， range is 0- 1000 | Default: 0-110 If country is Germany，range is0- 100 | -50-50 |
| SG10KTL-MT | 0x2C0F | 2 | 2 | 0-1100 | 0-110 | -50-50 |
| SG12KTL-M | 0x013C | 2 | 2 | 0-1100 | 0-132 | -60-60 |
| SG15KTL-M | 0x0142 | 2 | 2 | 0-1100 | 0-165 | -75-75 |

| SG17KTL-M | 0x0149 | 2 | 2 | 0-1100 | 0-187 | -85-85 |
| --- | --- | --- | --- | --- | --- | --- |
| SG20KTL-M | 0x0143 | 2 | 2 | 0-1100 | 0-220 | -100-100 |
| SG80KTL-M | 0x0139 | 4 | 4 | 0-1100 | 0-880 | -400-400 |
| SG111HV | 0x014C | 1 | 1 | 0-1000 | 0-1110 | -555-555 |
| SG125HV | 0x013B | 1 | 1 | 0-1000 | 0-1250 | -625-625 |
| SG125HV-20 | 0x2C03 | 1 | 1 | 0-1000 | 0-1250 | -625-625 |
| SG30CX | 0x2C10 | 3 | 2 | 0-1000 | 0-299 | -179~179 |
| SG33CX | 0x2C00 | 3 | 2 | 0-1100 | 0-363 | -218~218 |
| SG36CX-US | 0x2C0A | 3 | 2 | 0-1100 | 0-360 | -216~216 |
| SG40CX | 0x2C01 | 4 | 2 | 0-1100 | 0-440 | -264~264 |
| SG50CX | 0x2C02 | 5 | 2 | 0-1100 | 0-550 | -330~330 |
| SG60CX-US | 0x2C0B | 5 | 2 | 0-1100 | 0-600 | -360~360 |
| SG49.5CX-JP | 0x2C21 | 6 | 2 | 0-1000 | 0-495 | -297 ~ 297 |
| SG110CX | 0x2C06 | 9 | 2 | 0-1100 | 0-1100 | -660~660 |
| SG250HX | 0x2C0C | 12 | 2 | 0-1110 | 0-2500 | -1500~1500 |
| SG250HX-US | 0x2C11 | 12 | 2 | 0-1110 | 0-2500 | -1500~1500 |
| SG100CX | 0x2C12 | 12 | 2 | 0-1000 | 0-1000 | -660~660 |
| SG100CX-JP | 0x2C12 | 12 | 2 | 0-1000 | 0-1000 | -660~660 |
| SG250HX-IN | 0x2C13 | 12 | 2 | 0-1250 | 0-2500 | -1500~1500 |
| SG25CX-SA | 0x2C15 | 3 | 2 | 0-1100 | 0-275 | -165~165 |
| SG125HX | 0x2C1C | 6 | 2 | 0-1000 | 0-1250 | -750 - 750 |
| SG75CX | 0x2C22 | 9 | 2 | 0-1000 | 0-750 | -450~450 |
| SG3.0RT | 0x243D | 2 | 1 | Default: 0- 1100 (Germany, Belgium, Australia: 0-1000) | 0-33 | -15~15 |
| SG4.0RT | 0x243E | 2 | 1 |  | 0-44 | -20~20 |
| SG5.0RT | 0x2430 | 2 | 1 |  | Default: 0-55 (Germany, Australia: 0-50) | -25~25 |
| SG6.0RT | 0x2431 | 2 | 1 |  | Default: 0-66 (Germany, Australia: 0-60) | -30~30 |
| SG7.0RT | 0x243C | 2 | 2;1 |  | Default: 0-77 (Germany: 0-70; Australia: 0- 69.99) | -35~35 |
| SG8.0RT | 0x2432 | 2 | 2;1 |  | Default: 0-88 (Germany, Australia: 0-80) | -40~40 |
| SG10RT | 0x2433 | 2 | 2;1 |  | Default: 0-110 (Germany, Belgium, Australia: 0-100) | -50~50 |
| SG12RT | 0x2434 | 2 | 2;1 |  | Default: 0-132 (Germany, Australia: 0-120) | -60~60 |

| SG15RT | 0x2435 | 2 | 2 |  | Default: 0-165 (Germany, Australia: 0-150) | -75~75 |
| --- | --- | --- | --- | --- | --- | --- |
| SG17RT | 0x2436 | 2 | 2 |  | Default: 0-187 (Germany, Australia: 0-170) | -85~85 |
| SG20RT | 0x2437 | 2 | 2 |  | Default: 0-220 (Germany, Australia: 0-200) | -100~100 |
| SG22RT | 0x2438 | 2 | 2 |  | Default: 0-242 (Germany, Australia: 0-220) | -110-110 |
| SG23RT | 0x243B | 2 | 2 |  | Default: 0-253 (Germany, Australia: 0-230) | -115-115 |
| SG25RT | 0x2439 | 2 | 2 |  | Default: 0-275 (Germany, Australia: 0-250 | -125-125 |
| SG3.0RT-P2 | 0x244D | 2 | 1 | Default: 0- 1100 (Germany, Belgium, Australia: 0-1000) | 0-33 | -15~15 |
| SG4.0RT-P2 | 0x244E | 2 | 1 |  | 0-44 | -20~20 |
| SG5.0RT-P2 | 0x2440 | 2 | 1 |  | Default: 0-55 (Germany, Australia: 0-50) | -25~25 |
| SG6.0RT-P2 | 0x2441 | 2 | 1 |  | Default: 0-66 (Germany, Australia: 0-60) | -30~30 |
| SG7.0RT-P2 | 0x244C | 2 | 2;1 |  | Default: 0-77 (Germany: 0-70; Australia: 0- 69.99) | -35~35 |
| SG8.0RT-P2 | 0x2442 | 2 | 2;1 |  | Default: 0-88 (Germany, Australia: 0-80) | -40~40 |
| SG10RT-P2 | 0x2443 | 2 | 2;1 |  | Default: 0-110 (Germany, Belgium, Australia: 0-100) | -50~50 |
| SG12RT-P2 | 0x2444 | 2 | 2;1 |  | Default: 0-132 (Germany, Australia: | -60~60 |

|  |  |  |  |  | 0-120) |  |
| --- | --- | --- | --- | --- | --- | --- |
| SG15RT-P2 | 0x2445 | 2 | 2 |  | Default: 0-165 (Germany, Australia: 0-150) | -75~75 |
| SG17RT-P2 | 0x2446 | 2 | 2 |  | Default: 0-187 (Germany, Australia: 0-170) | -85~85 |
| SG20RT-P2 | 0x2447 | 2 | 2 |  | Default: 0-220 (Germany, Australia: 0-200) | -100~100 |
| SG23RT-P2 | 0x244B | 2 | 2 |  | Default: 0-253 (Germany, Australia: 0-230) | -115-115 |
| SG25RT-P2 | 0x2449 | 2 | 2 |  | Default: 0-275 (Germany, Australia: 0-250 | -125-125 |
| SG5.5RS-JP | 0x260D | 3 | 3 | 0-1000 | 0-55 | -35 - 35 |
| SG2.0RS-S | 0x2600 | 1 | 1 | 0-600 | 0-20 | -12~12 |
| SG2.5RS-S | 0x2601 | 1 | 1 | 0-600 | 0-25 | -15~15 |
| SG3.0RS-S | 0x2602 | 1 | 1 | 0-600 | 0-30 | -18~18 |
| SG3.0RS | 0x2603 | 2 | 1 | 0-600 | 0-30 | -18~18 |
| SG3.6RS | 0x2604 | 2 | 1 | 0-600 | 0-36 | -21~21 |
| SG4.0RS | 0x2605 | 2 | 1 | 0-600 | 0-40 | -24~24 |
| SG5.0RS | 0x2606 | 2 | 1 | 0-600 | 0-50 | -30~30 |
| SG6.0RS | 0x2607 | 2 | 1 | 0-600 | 0-60 | -36~36 |
| SG8.0RS | 0x2608 | 3 | 1 | 0-600 | 0-80 | -48~48 |
| SG9.0RS | 0x260E | 3 | 1 | 0-600 | 0-90 | -54~54 |
| SG10RS | 0x2609 | 3 | 1 | 0-600 | 0-100 | -60~60 |
| SG5.0RS-ADA | 0x260F | 3 | 1 | 0-600 | 0-50 | -30~30 |
| SG125HX-JP | 0x2C25 | 12 | 2 | 0-1100 | 0-1250 | -1500 - 1500 |
| SG320HX | 0x2C26 | 12 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |
| SG320HX | 0x2C26 | 14 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |
| SG320HX | 0x2C26 | 16 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |
| SG350HX | 0x2C27 | 12 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |
| SG350HX | 0x2C27 | 14 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |
| SG350HX | 0x2C27 | 16 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |
| SG125CX-P2 | 0x2C2D | 12 | 2 | 0-1100 | 0-1250 | -750 - 750 |
| SG110CX-P2 | 0x2C40 | 12 | 2 | 0-1100 | 0-1100 | -660-660 |
| SG75CX-P2 | 0x2C3F | 8 | 2 | 0-750 | 0-750 | -450-450 |
| SG285HX | 0x2C43 | 12 | 2 | 0-1000 | 0-2850 | -1710 - 1710 |
| SG333HX | 0x2C46 | 12 | 2 | 0-1040 | 0-3330 | -1998 - 1998 |
| SG333HX | 0x2C46 | 16 | 2 | 0-1040 | 0-3330 | -1998 - 1998 |
| SG350HX-US | 0x2C4F | 12 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |

| SG350HX-US | 0x2C4F | 16 | 2 | 0-1100 | 0-3520 | -2112 - 2112 |
| --- | --- | --- | --- | --- | --- | --- |
| SG25CX-P2 | 0x2C33 | 3 | 2 | 0-1100 | 0-275 | -165-165 |
| SG30CX-P2 | 0x2C34 | 3 | 2 | 0-1100 | 0-330 | -198-198 |
| SG33CX-P2 | 0x2C35 | 3 | 2 | 0-1100 | 0-363 | -217-217 |
| SG36CX-P2 | 0x2C36 | 4 | 2 | 0-1100 | 0-396 | -237-237 |
| SG40CX-P2 | 0x2C37 | 4 | 2 | 0-1100 | 0-440 | -264-264 |
| SG50CX-P2 | 0x2C32 | 4 | 2 | 0-1100 | 0-550 | -330-330 |

Appendix 6 Q(P)	Curve 1

| COS Ф Upper PF Cap 1 Lower PF Ind |  | （PA,K_A) Capacitive | Curve A |  | 5048~5064, Not Italy curve Q/Pn Curve B （PA,K_A) Lower Cap P/Pn 0 （PB,K_B) Inductive Upper Ind (PC,K_C) |  |  | P/Pn (PC,K_C) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | 0 - 1, |  |  | Curve A:PA <PC |
| Curve | 5048 |  |  | U16 |  | 0 Curve A, |  |  | Curve B: |
|  |  |  |  |  |  | 1 Curve B |  |  | (PA≤PB≤PC, but PA!=PC) |
| PB | 5049 |  |  | U16 |  | 200-1000 Curve B is valid | 0.1% |  | and (KA≤KB≤KC |
| KB | 5050 |  |  | S16 |  | -500-500 Curve B is valid | 0.001 |  | or KA≥KB≥KC,but KA!=KC) |
| PA(Lower Power) | 5051 |  |  | U16 |  | Curve A:0~500 Curve B:100-1000 | 0.1% |  |  |
| PC(Upper Power) | 5052 |  |  | U16 |  | Curve A:500~1000 Curve B:200-1000 | 0.1% |  |  |
| KA(Upperlimit-PF) | 5053 |  |  | S16 |  | Curve A:900~1000 Curve B:-500-500 | 0.001 |  |  |
| KC(Lower limit-PF) | 5054 |  |  | S16 |  | Curve A:900~1000 Curve B:-500-500 | 0.001 |  |  |
| Reserved | 5055-5064 |  |  |  |  |  |  |  |  |
| 5065~5077,Italy curve |  |  |  |  |  |  |  |  |  |
| powerA | 5065 |  |  | U16 |  | 200~1000 | 0.1% |  | powerA<=powerB<powerC |
| powerB | 5066 |  |  | U16 |  | 200~1000 | 0.1% |  |  |
| powerC | 5067 |  |  | U16 |  | 200~1000 | 0.1% |  |  |
| pf_max | 5068 |  |  | U16 |  | 900~1000 | 0.001 |  |  |
| Uin | 5069 |  |  | U16 |  | 1000~1100 | 0.1% |  | Uin>Uout |
| Uout | 5070 |  |  | U16 |  | 900~1000 | 0.1% |  |  |
| Reserved | 5071~5077 |  |  | U16 |  |  |  |  |  |

Appendix 7	Q(U)	Curve 1

| 5078~5097, Not Italy curve Curve A Curve B Q /Pn Q1 Q /Pn Upper Q/Sn Ind Q1 Upper Q/Sn Ind Hysteresis Q_U1 Q2 Q3 U1 Limit / U2 Limit Upper U Limit Lower U Limit U1 Limit Vn U2 Limit Upper U Limit V/Vn Lower U Limit Q2/Q3 V/Vn Q_U2 Hysteresis Lower Q/Sn Cap Q4 Lower Q/Sn Cap Q4 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Curve |  | 5078 |  | U16 | 0-1, 0 Curve A, 1 Curve B |  | Curve A: (U1Limit+Hysteresis<U2 Limit- Hysteresis) and (-Upper Q/Sn<=Q_U1<= Lower Q/Sn) and (-Upper Q/Sn<=Q_U2<= Lower Q/Sn) Curve: U1 Limit == U2 Limit |
| Q_U1 |  | 5079 |  | S16 | -500-500, Curve A is valid | 0.1% |  |
| Q_U2 |  | 5080 |  | S16 | -500-500， Curve A is valid | 0.1% |  |
| Lower ULimit |  | 5081 |  | U16 | 800~1000 | 0.1% |  |
| Upper U Limit |  | 5082 |  | U16 | 1000~1200 | 0.1% |  |
| U1 Limit |  | 5083 |  | U16 | 900~1100 | 0.1% |  |
| U2 Limit |  | 5084 |  | U16 | 900~1100 | 0.1% |  |
| Hysteresis |  | 5085 |  | U16 | 0~50 Curve A is valid | 0.1% |  |
| Lower Q/Sn |  | 5086 |  | U16 | (Ind) 0~ 500 | 0.1% |  |
| Upper Q/Sn |  | 5087 |  | U16 | (Cap) 0~500 | 0.1% |  |
| Reserved |  | 5088-5097 |  |  |  |  |  |
| 5098~5115, Italy curve |  |  |  |  |  |  |  |
| V1i (Italy) | 5098 |  | U16 |  | 900~1100 | 0.1% |  |
| V2i (Italy) | 5099 |  | U16 |  | 900~1100 | 0.1% | V2i < V1i < V1s < V2s |
| V1s (Italy) | 5100 |  | U16 |  | 900~1100 | 0.1% |  |
| V2s | 5101 |  | U16 |  | 900~1100 | 0.1% |  |

| (Italy) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Qmax (Italy) | 5102 | U16 | 500~1000 | 0.001 |  |
| Pin (Italy) | 5103 | U16 | 200~1000 | 0.1% | Pin > Pout |
| Pout (Italy) | 5104 | U16 | 10~200 | 0.1% |  |
| Curve (Italy) | 5105 | U16 | 0-1, - Curve A, - Curve B |  |  |
| Reserved | 5106~5115 |  |  |  |  |

Appendix 8	Q(P) Curve 2○1

| Curve A Curve B COS Ф Q/Pn （QP_P1,QP_K1) （QP_P1,QP_K1) Upper PF Lower Cap Cap Capacitive L1 L1 （QP_P2,QP_K2) P/Pn （QP_P2,QP_K2) P/Pn 1 Lower Power Upper Power 0 Lower Power Upper Power L2 Inductive L2 Lower PF Ind Upper Ind (QP_P3,QP_K3) (QP_P3,QP_K3) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Q(P) Curve | 5116 | U16 | 0-1 0: Curve A 1: Curve B |  | - QP_P1<= QP_P2< QP_P3 - If QP_P1= QP_P2, QP_K1= QP_K2 QP_EnableMode: Enter and exit Q (P) mode conditions, 0xAA, unconditional entry and exit; 0x55, conditional entry and exit: the voltage is higher than QP_EnterVoltageRatio, the voltage is lower than UoutQP_ExitVoltageRatio, and the power is lower than QP_ExitPowerRatio |
| QP_P1 | 5117 | U16 | 100~1000 | 0.1% |  |
| QP_P2 | 5118 | U16 | 200~1000 | 0.1% |  |
| QP_P3 | 5119 | U16 | 200~1000 | 0.1% |  |
| QP_K1 | 5120 | S16 | Curve A:800~1000 Curve B: If support Overload -660-660 If not -600-600 | 0.001 |  |
| QP_K2 | 5121 | S16 | Curve A:800~1000 | 0.001 |  |

|  |  |  | If support Overload -660-660 If not -600-600 |  |  |
| --- | --- | --- | --- | --- | --- |
| QP_K3 | 5122 | S16 | Curve A:800~1000 If support Overload -660-660 If not -600-600 | 0.001 |  |
| QP_EnterVoltageRatio | 5123 | U16 | 1000~1100 | 0.1% |  |
| QP_ExitVoltageRatio | 5124 | U16 | 900~1000 | 0.1% |  |
| QP_ExitPowerRatio | 5125 | U16 | 10-200 | 0.1% |  |
| QP_EnableMode | 5126 | U16 | 0xAA Yes 0x55 No |  |  |
| Reserved | 5127-5134 | U16 |  |  |  |

○1 Except SG0.7/1.0/1/5/2.0/2.5/3.0RS-S, SG3.0/3.6/4.0/5.0/6.0RS, SG5.0RS-ADA, SG8.0/9.0/10RS

Appendix 9	Q(U) Curve 2○1

| Q/Sn Curve A Q/Sn Curve B (QU_V1, QU_Q1) (QU_V1, QU_Q1) (QU_V2, QU_Q2) Upper Q/Sn Ind Upper Q/Sn Ind 滞环比 (QU_V3, QU_Q3) Grid voltage Grid voltage (QU_V2, QU_Q2) Hysteresis Lower Q/Sn Cap Lower Q/Sn Cap (QU_V3, QU_Q3) (QU_V4, QU_Q4) (QU_V4, QU_Q4) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Q(U) Curve | 5135 | U16 | 0-1 0: Curve A; 1: Curve B |  | QU_V1ve B,; Inioiooower QU_EnableMode: Enter and exit Q (U) mode conditions, 0xAA, unconditional entry and exit; 0x55, conditional entry and exit: the current power is higher than QU_EnterPower, and the current power is lower than QU_ExitPower. 0x5A, conditional entry PF is lower than QU_LimitPFValue |
| Hysteresis Ratio | 5136 | U16 | 0~50 | 0.1% |  |
| QU_V1 | 5137 | U16 | 800~ 1000 | 0.1% |  |
| QU_Q1 | 5138 | S16 | If support Overload -660-0 If not -600-0 | 0.1% |  |
| QU_V2 | 5139 | U16 | 800~1000 | 0.1% |  |
| QU_Q2 | 5140 | S16 | If support Overload -660-660 If not -600-600 | 0.1% |  |
| QU_V3 | 5141 | U16 | 1000~1200 | 0.1% |  |
| QU_Q3 | 5142 | S16 | If support Overload -660-660 If not -600-600 | 0.1% |  |
| QU_V4 | 5143 | U16 | 1000~1200 | 0.1% |  |
| QU_Q4 | 5144 | S16 | If support Overload 0-660 If not 0-600 | 0.1% |  |
| QU_EnterPower | 5145 | U16 | 200-1000 | 0.1% |  |
| QU_ExitPower | 5146 | U16 | 10-200 | 0.1% |  |
| QU_EnableMode | 5147 | U16 | 0xAA Yes 0x55 No |  |  |
| QU_LimitPFValue | 5148 | U16 | 0-95 | 0.01 |  |
| Reserved | 5149~5154 |  |  |  |  |

○1  Except SG0.7/1.0/1/5/2.0/2.5/3.0RS-S, SG3.0/3.6/4.0/5.0/6.0RS, SG5.0RS-ADA, SG8.0/9.0/10RS

Appendix 10 Comparison table of series models

| Series name | Specific model |
| --- | --- |
| SG33-50CX | SG25CX-SA SG30CX SG33CX SG40CX SG50CX SG36CX-US SG60CX-US |
| SG100-136TX | SG75CX SG100CX SG110CX SG136TX SG100CX-JP |
| SG225-350HX | SG225HX SG250HX-US SG250HX SG250HX-IN SG250HX-IN-20 SG125HX SG125HX-JP SG320HX SG350HX SG285HX SG333HX SG350HX-US |
| SG5-20KTL-M | SG5KTL-MT SG6KTL-MT SG8KTL-M SG10KTL-M SG10KTL-MT SG12KTL-M SG15KTL-M SG17KTL-M SG20KTL-M |
| SG80-110HV | SG80HV SG80BF SG110HV-M |
| SG125HV | SG125HV SG125HV-20 |
| Black King Kong | SG60KTL SG50KTL-M |

|  | SG60KTL-M SG60KTL SG60KU SG60KU-M SG80KTL |
| --- | --- |
| Ruby | SG33KTL-M SG40KTL-M SG50KTL SG33KTL-M SG36KTL-M |
| Japan kJ | SG33K3J SG49K5J SG111HV |
| SGRT | SG3.0RT SG4.0RT SG5.0RT SG6.0RT SG7.0RT SG8.0RT SG10RT SG11RT SG12RT SG15RT SG17RT SG20RT SG22RT SG23RT SG25RT |

# Examples

Take ComTest for example.

  - Acquire one piece of running information

Supposed that the inverter address is 1, it needs to acquire data from address 5000 of 3x address type. The PC sends (HEX):

01 04 13 87 00 01 85 67

The inverter replies (HEX):

01 04 02 01 32 39 75

Note: The type code of inverter SG60KU-M is 0x0132.

  - Acquire multiple running information

Supposed that the inverter address is 1, it needs to acquire10 data from address starting from 5000 of 3x address type

The PC sends (HEX):

## 01 04 13 87 00 0A C4 A0

The inverter replies (HEX):

## 01 04 14 01 32 00 28 00 00 00 00 00 05 00 00 00 26 00 00 00 00 00 00 56 EA

Note: The type code of inverter SG60KU-M is 0x0132. The nominal output power is 4.0kW, two-phase. Daily power generation is 0. The total power generation is 5kWh. The total running time is 38h.The internal temperature is 0℃. The internal transformer temperature is 0℃.

  - Acquire SN

Supposed that the inverter address is 1, it needs to acquire 10 data from address starting from 4990 of 3x address type

The PC sends (HEX):

## 01 04 13 7D 00 0A E4 91

The inverter replies (HEX):

## 01 04 14 31 32 31 32 31 32 30 30 31 00 00 00 00 00 00 00 00 00 00 00 9B 56

Note:

    - SN data type is UTF-8;

    - Serial number is: 121212001

  - Read one setting datum

Supposed that the inverter address is 1, it needs to read data from address 5000 of 4x address type. The PC sends (HEX):

## 01 03 13 87 00 01 30 A7

The inverter replies (HEX):

## 01 03 02 07 D8 BA 2E

Note: the data read out is year 2008.

  - Read multiple setting data

Supposed that the inverter address is 1, it needs to read 10 data from address starting from 5000 of 4x address type.

The PC sends (HEX):

## 01 03 13 87 00 0A 71 60

The inverter replies (HEX):

## 01 03 14 07 DA 00 0A 00 1E 00 09 00 28 00 25 00 CE 00 AA 01 F4 00 00 80 53

Note: The data are October, 10, 2010, 09:40:37; Stop; power limitation on, power limitation value is 50 %.

  - Set one datum

Supposed that the inverter address is 1, it needs to set data from address 5000 of 4x address type. The PC sends (HEX):

## 01 10 13 87 00 01 02 07 DA 19 4D

The inverter replies (HEX): 01 10 13 87 00 01 B5 64

Or

The PC sends (HEX):

## 01 06 13 87 07 DA BE CC

The inverter replies (HEX): 01 06 13 87 07 DA BE CC

Note: The setting data is year 2010

  - Set multiple data

Supposed that the inverter address is 1, it needs to set 10 data to address starting from 5000 of 4x address type. The PC sends (HEX):

## 01 10 13 87 00 0A 14 07 D9 00 0A 00 1E 00 09 00 10 00 00 00 CE 00 AA 01 F4 00 00 3E 65

The inverter replies (HEX):

## 01 10 13 87 00 0A F4 A3

Note: The data are October, 30, 2009, 09:16:00, stop, power limitation on, power limitation value is 50 %.

  - Read device running information

Supposed that the inverter address is 1, it needs to set 8 data to address starting from 5038 of 3x address type. The PC sends (HEX):

## 01 04 13 AD 00 0864 A9

The inverter replies (HEX):

## 01 04 10 55 00 07 DF 00 0C 00 15 00 04 00 0C 00 3B 00 0A EE D1

Note:

- Device running state is Fault(0x5500); the fault/alarm time and code are valid in this state;

- Fault time: 4 (0x0004):12(0x000C): 59(0x003B), Dec. (0x000C), 21(0x0015), 2015(0x07DF); the fault is

island (0x000A).